## Semi Indoor-Sch IA
Schedule-IA : Supply and Construction of Control Room etc. for new 33/11KV Semi -Indoor Sub-station
Sl. No. | Description of work | Unit | Quantity
I | Constructions of Control room
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | 1 Cum | 160
2 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) as per Directions of Eng-in-Charge. | 1 Cum | 135
3 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including, excluding Seionarage charges, conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310)as per Directions of Eng-in-Charge. | 1 Cum | 22.5
4 | Filling of gravel in trenches, sicks of foundations, basements etc. of approved quality in layers not exceeding 15 c.m. thick consolidating each deposited layer by watering and ramming including cost and conveyance of gravel ,excluding seignoirage charges, water to work site and operational, incidental, labour charges etc. complete for furnished item of work | 1 Cum | 115
5 | Supply and spreading of quarry dust to a thickness of 25mm, excluding seigniorage (after consolidation of the earth work with a roller.) | CUM | 8
6 | Supply and spreading of 20mm size machine crushed blue granite metal to a thickness of 75 mm over spread quarry dust excluding seigniorage. | CUM | 4.75
7 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | 1 Cum | 25
8 | Providing HYSD/TMT/MS Steel bars(Fe415/Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 5
9 | Providing Antitermite treatment as per IS 6315 (Part - 2) 2001 (Pre-constructional chemical treatment measures) along the internal & external vertical faces of the columns, plinth beams, basement and top surface of the basement filling below flooring bed as per the specified procedure conforming to IS 6315 (Part-2) 2001 and other relevant approved specification duly using Chlorpyriphos/ Lindane emulsifiable concentrate 20% with 1% concentration @ 7.5 Liters/ sqm of the vertical surface & @ 5.0 Liters/ sqm of the horizontal surface of the substructure to a depth of 500 mm around columns & 300 mm deep around plinth beams, basements & floor filling area including excavation channel along the wall & rodding etc & cost & conveyance of all materials to the site, cost of labour for spraying, rodding etc complete for finished item of work as per the approval of the Engineer-in-Charge | 1 Sqm | 115
10 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in-Charge. | 1 Cum | 30
11 | Construction of Brick masonry walls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | 1 Cum | 75
12 | RCC M- 25 Desgin mix (380 Kg Cement) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including sales & other taxes on all materials excluding Seionarage charges, including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work as directed by Engineer-in- Charge..
i | Footings | 1 Cum | 20.65
ii | Pedastal | 1 Cum | 2.63
iii | Plinth beams | 1 Cum | 8.05
iv | Lintel beams | 1 Cum | 1.25
v | Columns | 1 Cum | 12.75
viii | Piles | 1 RM | 135
viii | Pile caps | 1 Cum | 8.02
viii | Sunshades and Chajjas | 1 Sqm | 8.5
ix | Roof beams | 1 Cum | 10
x | Roof Slab | 1 Cum | 19.75
13 | Construction of cable duct in the control room shall be of size 300 x 300mm with PCC 1:4:8 using 40mm metal 100mm thick and 115mm thick brick masonry on 2 sides and Plastering 3 sides with CM 1:5 closing of duct with cement slabs of 50mm - thick using RCC 1:2:4 using 10mm HBG metal includes cost of all materials and labour and the cost of cement excluding seionarge charges (as per Technical specification) | RMt | 20
14 | Providing impervious coat to exposed RCC roof slab surface with CM(1:3), 20mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying, rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc,, complete for finished item of work excluding Seionarage charges for finished item of work as directed by Engineer-in-Charge.. . | 1 Sqm | 115
15 | Plastering to ceiling 12 mm thick in one coat in CM(1:3) with Smooth finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves excluding seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 150
16 | Plastering 12 mm thick in one coat for superstructurefor even faces of walls with CM(1:5) with smooth finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves, excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge | 1 Sqm | 200
17 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 280
18 | Plain Cement concrete (1:2:4) using 10 mm & 12mm metal with concrete mixer including cost and conveyance of all materials and all labour charges complete excluding Seionarge charges. | 1 Cum | 12.5
19 | Flooring with vitrified polished floor tiles glossy finish premium colours of size not less than 598x598mmx8mm thickness of 1st quality(make Somany,HR Jhonson,Naveen Ceramics, Kajaria, Nitco, Sphinx) set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand water and tiles etc., complete, complete for finished item of work including the cost of conveyance of all materials excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 75
20 | Providing skirting to internal walls to 10 cm height/risers of steps vitrified polished floor tiles glossy finish premium colours of size not less than 598x598mmx8mm thickness of 1st quality(make Somany,HR Jhonson,Naveen Ceramics, Kajaria, Nitco, Sphinx) set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand water and tiles etc., complete, complete for finished item of work including the cost of conveyance of all materials excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. . | 1 Sqm | 25
21 | Flooring with Non-skid red or white full body Ceramic floor tiles of size 300 x 300 mm and thickness between 7-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, potable water, sand and tiles etc., complete for finished item of work. | 1 Sqm | 15
22 | Dadooing in toilets and bath rooms with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs set over a base coat of CM (1:3) 12 mm thick with neat cement slurry of honey like consistency spread at the rate of 3.3 Kgs per Sqm and filling the joints with white cement paste mixed with pigment of matching shade is to be done including cost and conveyance charges of cement, potable water and all other materials to site, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 15
23 | Painting with Interior grade synthetic polymer plastic emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/ litre of approved brand and shade two coats over a base coat of appropriate interior primer(grade-I) of Asian make, making 3 coats in all to give an even shade after thorughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and convyance of all materials, labour charges and incidental charges such as scaffolding, lift charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 350
24 | Painting with acrylic exterior emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/ litre exterior grade of approved brand and colour/shade two coats over a base coat of appropriate primer (grade-I) of Asain make , making 3 coats in all to give an even shade after thorughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and convyance of all materials, labour charges and incidental charges such as scaffolding, lift charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 280
25 | White washing two coats with whiting of approved quality to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials including cost of all materials, labour charges and incidental such as scaffolding, lift charges etc., complete for finished item of work, but excluding conveyance charges of materials | 1 Sqm | 150
26 | Painting with synthetic enamel paint of approved brand and shade one coats over a base coat of approved primer making it two coats in all to give an even shade after thorughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and convyance of all materials, labour charges and incidental charges such as scaffolding, lift charges etc., complete for finished item of work. | 1 Sqm | 15
27 | Supplying and fixing of Un plasticised Poly Vinyl Chloride (UPVC) sliding doors two track - only two glass shutters sliding - 95 -Series duly manufactured using UPVC reinforced profiles of 95.50 mm x 60 mm x 2.25 mm for outer frames, 66 mm x 42 mm x 2.25 mm for sliding door shutter frames capable of mounting single glazing system, structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.2 mm prefabricated & welded through fusion welding the window sash shall be fitted with 5 mm thick clear float glass of reputed make duly fixed with EPDM weathering seal resistant accessories like clipping locking system made of aluminium 1 No., per set of sashes and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/ deglazing at site etc., with iron safety grill with 10mm size square rod including two coats of synthetic enamel painting and including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site with templates for casement sizing complete for finished item of work | 1 RM | 20
28 | Providing R.C.C. racks of 38mm thick with R.C.C.(1:2:4) and plastering with CM(1:3),12mm thick excluding seigniorage cost and conveyance of all materials to site and all labour charges complete excluding seionarage charges and as directed by the Engineer in charge.. | 1 Sqm | 4
29 | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of size with encapsulation of 8MM rigid layer on all the six surfaces. The door frame will have a rebat of 32MM. Door Frame section of 63.5x100 MM .The two Vertical members are to be joined together with the horizontal member using 8x75 MM long MS Star full thread screws to be used with reverse forward speed control hand drilling machine. The ready/assembled door frame is fixed to the wall using hold fast or bolt fasteners. A minimum of 4 No.s of screws to be provided for each vertical member & minimum 2no.s for horizontal member.
a | Door Frame section of 63.5x100 MM .The two Vertical members are to be joined together with the horizontal member using 8x75MM long MS Star full thread screws etc., rate vide item code BMT-N.83.C | 1 RM | 1.5
b | Providing and fixing 28 -30 MM thick solid Wood Polymer Composite(WPC) single extruded door shutter with 3MM top and bottom rigid layer with an overall density of 750kg/Cum. It will be fixed to the frame using 3 inch /4 inch hinges. A minimum of 4 hinges will be required for fixing the door with the frame including labour charges, 4Nos 125mm aluminium butt hinges, 1No 250mm aluminium aldrop, 1No 200mm aluminium tower bolt, 2Nos 150mm aluminium handles etc., complete for finished item of work as directed by the Engineer in charge. | 1 Sqm | 2
30 | Supply and fixing of M.S. grill windows with 10mm square solid rods with 25mm x 25mm x 5mm L Angle and casting and fixing of MS Ladder with channels and L Angles to reach for water tank on terrace and approved design given by the department and as directed by the engineer at site including cost and conveyance of all materials and all labour charges etc., complete. | 1 Sqm | 20
31 | Supply and fixing of European Water Closet of Ist quality with plastic seat and lid and PVC flushing tank 10 Lit capacity confirming to IS:2556-Part-2-1973 of Hidustan/Neycer or Parry ware make white glazed with 'S' trap including all materials ,labour etc complete as per directions of Eng-in-Charge. | Set | 1
32 | Supply and fixing of dia (4kg/sqcm) PVC pipes of make Prince/Sudhakar/Kisan/Supreme or any ISI Brand including bends, Tees etc., including cost and conveyance of all materials all labour charges etc., complete. as directed by the Engineer in charge.
a | 75 mm dia | RMt | 5
b | 110 mm dia | RMt | 15
33 | Supply and fixing 550 x 400mm size Indian make Flat Back Wash Hand basin with pedestal (HSW/Parryware/Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15mm nominal bore chromium plated pillar tap of 1st quality Indian make 400 grams Seiko/Senior/Nice/Esso or equivalent complete with standard CI brackets : 550 x 400 mm - double C.P. Pillar cock etc complete as directed by the Engineer in charge. | Set | 1
34 | Supply and fixing of Unplasticised PVC Pipes,10 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color including Labour charges for laying, fixing, and commissioning the pipes including couplers, bends, plugs, junctions, tees etc. with solvent jointing as per Standard practice for finished item work as directed by the Engineer-in-charge.
a | 25 mm dia | RMt | 125
b | 20mm dia | RMt | 50
35 | Supply and fixing of CP Long body bib cock fancy type delux heavy duty 12.7mm dia Indian make 400gm seiko or equivalent etc., complete for finished item of work as directed by the Engineer - In - Charge | Each | 1
36 | Supply and fixing of CP Short body bib cock fancy type delux heavy duty 12.7mm dia Indian make 400gm seiko or equivalent etc., complete for finished item of work as directed by the Engineer - In - Charge | Each | 1
37 | Supply and fixing of GM Gate ( GM peet) valves as per IS 778 Class I -Indian make heavy type of different sizes including cost and conveyance of all materials and labour Charges complete for finished item work as directed by the Engineer-in-charge.
a | 25 mm GM Gate valve | Each | 2
38 | Supplying and Fixing 76.2 mm Nahny Trap 1st quality in RCC floors page No.121, Sl No.126) | 1 No | 1
39 | Supply and fixing of soap stands in the washroms including cost and conveyance of all materials, labour charges etc., | 1 No | 1
40 | Supply and fixing of 25.4 mm dia& 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws including cost and conveyance of all materials, labour charges etc., complete | 1 No | 1
41 | Providing and placing on terrace (at all floor levels) 1000 Ltr capasity Polyethylene water storage tank double layer of SYNTEX or approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but without fittings and base support for tanks etc., complete for finished item of work as directed by the Engineer-in- charge. | 1 No. | 1
42 | Supply and fixing 450 x 300 mm Belgium glass 6mm thick frameless mirror with stand mounted to wall including plugs and screws as directed by the Engineer in charge. | RMt | 1
43 | Supply and fixing CP Short body bib cock facy type deluxe heavy duty 12.7mm dia Indian make Seiko/Senior/Nice or equivalent | Each | 24
44 | Constructing 2’ x 2' brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 /sq.mmincluding plastering with cement mortar 1:3 prop; ½” thick both inside and outside fitted with 20” dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc. to site, and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification excluding Seionarage charges as directed by the Engineer in charge. | 1 No | 2
45 | Supply and Fixing of 25mm dia 2mm thick P.V.C. pipe (ISI MARK) concealed in reinforcement and walls with all required accessories including masonary work for light, fan and separate plug point including all labour charges etc., complete. | RMt | 200
46 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular switch, Ceiling rose and hot dip galvanized metal boxes with cover frame to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings (makes Anchor / Gold Medal / Million / Vimal / Maru / Milltec.) as directed by the Engineer in charge. | Each | 30
47 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular switch and 3/2 pin socket hot dip galvanized metal boxes with cover frame to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings (makes Anchor / Gold Medal / Million / Vimal / Maru / Milltec.) as directed by the Engineer in charge. | Each | 4
48 | Wiring with 2 of 22/0.3mm (1.5 Sq.mm)P.V.C. insulated F.R. flexible copper cable (ISI MARK) in existing pipe with 16A modular switch control and 3 pin/16A sockets with hot dip galvanized box with cover frame on separate board including all labour charges etc., complete. | Each | 8
49 | Supply and run of 2 of 22/0.3mm (1.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for MAINS Makes: Finolex / RR kabel /Havells/KEI/Polycab/Gloster /Goldmedal/GM inlcuding all labour charges etc., complete. | 1 RM | 400
50 | Supply and run of 1 of 22/0.3mm (1.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for earthing Makes: Finolex / RR kabel /Havells/KEI/Polycab/Gloster /Goldmedal/GM inlcuding all labour charges etc., complete. | 1 RM | 50
51 | Supply and fixing of 8way TPN Distribution board with IP-20 protection suitable for 3 phase ELCB / RCCB / FP with 40A, 4pole isolator as incomer and 10kA-6-32A (12Nos) SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc., complete as directed by the Engineer in charge. | Each | 1
52 | Supply and fixing of 18W/20W, 1200mm length LED( with LED light) batten light with extruded alluminium housing and polycarbonate cover, input voltage AC 220 - 260 Volts with PF>0.9, Surge protection: 2KV,THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 5700K, minimum CRI>70, .etc., complete. a) LUMINAIRE MAKE : Phillips / GE-Venture / Crompton / Wipro / Bajaj / Havells / Halonix/Jaquar/HPL/GM / GreenLites / Gold Medal/Eveready b) LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG/Everlight as per directions of Eng-in-Charge. | Each | 15
53 | S&F of 9W LED Lamps with Holder of standard make including cost of all fixture etc., complete as per directions of Eng-in-Charge. | Each | 6
54 | Supply and fixing 48" (1200mm) Sweep Ceiling Fan of makes (Crompton High speed/Bajaj Ultima/Havells Velocity/ Usha Astra/ Orient Summer Pride) with Modular Electronic Regulator of makes (Crab Tree/Feno Swtch/ Toyoma/Fortune Art/ Million / Gold Medal / Vimal / Anchor Roma) as directed by the Engineer in charge. | Each | 4
55 | Supply of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark. Makes : As per list of recommended brands. of makes (Crompton High speed/Bajaj Ultima/Havells Velocity/ Usha Astra/ Orient Summer Pride) with Modular Electronic Regulator of makes (Crab Tree/Feno Swtch/ Toyoma/Fortune Art/ Million / Gold Medal / Vimal / Anchor Roma) | 1 No | 6
56a | Supply,placing in alignment of RCC fencing post of 1.8m length including cost and conveyance of fencing post, labour charges for placing in alignment all are as specified by the Engineer-in-charge at site - - etc., complete. | Each | 28
56b | Supply and fixing galvanised steel barbed wire (IS:278-1962 Type I) weighing 9.36kg per 100 mtrs (min), Straining and fixing to any type of standard, including securing galvanised mild steel wire etc., as directed by engineer - in - charge | RMt | 650
57 | Providing independent earthing by excavating a trench to a depth of 2.7 M in all soils, as per size specified in the Data, using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of Salt and Charcoal in layers and all labour charges etc., complete for small quarters. | Each | 2
58 | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete. | 1RM | 50
59 | Supply of steel office Table of size 4' x 2' x 30" with 18 mm plywood , Teakwood finishing with Drawers on right hand side and with automatic locking system(Godrej or equivalent make)as directed by engineer - in - charge. | Each | 1
60 | Supply of chairs with arms teak wood Frame 1" thick,seat & backs, 's' type in 1" dia pipe(Godrej or equivalent make)as directed by engineer - in - charge. | 1 Sqm | 2
61 | Supply of Quartz wall clock 1' x 1'size of reputed make. | Each | 1
62 | Writing Name of the SS in Details on the Control room one side including cost & conveyance of all materials and all labour charges complete. | Each | 1
63 | Writing Name of the SS in Details on the Gate as directed by the Engineer in charge. | Each | 1
64 | Supply and keeping the 300 mm dia hume pipe in position including fixing collers etc.complete. For Running of Control Cables, XLPE Cable etc from Switch yard to Control Room, including excavation and backfilling etc | 1RM | 4
65 | Site investigation charges for locating bore well point. | 1 Job | 1
66 | Drilling of 165mm size Bore Well as directed by the Engineer in charge including cost of labour , flushing of borewell, transportation and hire charges for drilling equipment and all taxes complete as per the directions of the Engineer in charge for the finished item of work. | 1RM | 60
67 | Supplying & fixing of PVC heavy duty casing pipe of 180mm dia , 10kg/sqcm for the above Bore hole including cost & conveyance of all materials ,labour ,leads, and lifts and all taxes etc., complete as per the directions of the Engineer in charge for the finished item of work. | 1 RM | 60
68 | Supply, transportation & fixing of Single Phase submersible motor pump set , 21 stage (Crompton / Kirloskar / CRI / L&T / Varsha /Texmo make) of approved type suitable for 165mm dia bore well , as directed by Engineer in charge,of approved quality & make including nipples, bends, couplings etc., including cost & conveyance of all materials, labour charges, fitted with SIEMENS/ CROMPTON make starter with panel board fitted with related fittings such as Ammeter , volt meter and including nuts & bolts and GI sheet bore cover complete as per the directions of the Engineer in charge for the finished item of work.
a | 1.0 HP | Each | 1
b | 1.5 HP | Each | 1
69 | Supplying & fixing 40 mm dia HDPE pipe (12kg/Sqcm) of approved quality & make including nipples, bends, couplings etc., complete for finished item of work from bore well to delivery including cost & conveyance of all materials, specials\l fixtur | 1 RM | 55
70 | Supply & fixing of Submersible Flat cable 2.5sq.mm or 3/20 equalint (Finolex) wire including cost & conveyance and all labor charges with all leads ans lifts and all other incidental charges etc; complete. | 1 RM | 80
FOR SITES WHERE BORE WELL DIGGING IS NOT POSSIBLE TAP CONNECTION WITH TAP WATER STORAGE SUMP
71 | Earth work excavation in ordinary soils by manual means upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including all operational, incidental, labour charges such as shoring ,sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20 B (APSS 308) for water tank of size ( 2.0 MX2.5M X2.3 M ). | 1 Cum | 25
72 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum | 25
73 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including, seigniorage cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum | 1.5
74 | Plain Cement concrete (1:4:8) using 40 mm metal with concrete mixer including seigniorage, cost and conveyance of all materials and all labour charges complete. | 1 Cum | 1.5
75 | Construction of brick masonry in CM 1:6 using well burnt country bricks including seigniorage, cost and conveyance of all materials all labour charges etc., complete. Ground Floor | 1 Cum | 6
76 | Plastering with CM (1:5), 12 mm thick in one coat for inernal faces of walls, ceilings etc.,including seigniorage, cost and conveyance of all materials all labour charges etc, complete. Ground Floor | 1 Sqm | 35
77 | Providing HYSD/TMT/MS Steel bars(Fe415/Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 0.1
78 | RCC M- 25 Desgin mix (380 Kg Cement) for slab corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including Seigniorage charges, sales & other taxes on all materials including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work. | 1 Cum | 1
79 | Single Phase 1 HPMono-block Motor including giving Pipe line Connections with all bends, couplings and Running Joints etc., complete. | Each | 1

## Semi Indoor-Sch IB
Schedule-IB : Supply and Construction of Approach Road, Retaining Wall, Levelling of Site etc. for new 33/11KV Semi-Indoor Sub-station
Sl. No. | Description of work | Unit | Retaining wall with pile foundation | Retaining wall with Column foundation | Retaing wall with RR Masonary
Construction of Approach road, Reaining wall, Levelling of site etc.
1 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 400 | 400 | 400
2 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310)as per directions of Eng-in-Charge. | Cum | 40 | 40 | 40
Formation of WBP Approach road:
3 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 150 | 150 | 150
4 | Providing, laying, spreading and compacting stone aggregates of 65 mm Single nominal size to water bound macadam specification including spreading in uniform thickness, hand packing, rolling with three wheel 80-100 kN roller in stages to proper grade and camber, applying and brooming, crushable screening to fill-up the interstices of coarse aggregate, watering and compacting to the required density as per Technical Specification of MORDto a compacted thickness of 100 mm excluding seionrage charges etc. complete for finished item of work as directed by Engineer-in-charge. | Cum | 30 | 30 | 30
Construction of hume pipe culvert:
5 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | Cum | 17 | 17 | 17
6 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P ,excluding seionarge charges etc., complete for finished item of work. (APSS NO. 309 & 310) etc. complete for finished item of work as directed by Engineer-in-charge. | Cum | 3 | 3 | 3
7 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | Cum | 3 | 3 | 3
8 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in- Charge. | Cum | 10 | 10 | 10
9 | Construction of Brick Masonrywalls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | Cum | 8 | 8 | 8
10 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 8 | 8 | 8
11 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | Sq. M | 30 | 30 | 30
Construction of Retaining wall around Switch yard:
With Pile foundation / Column Footings
12 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | Cum | 28 | 28
13 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | Cum | 2.5 | 2.5
14 | Providing HYSD/TMT/MS Steel bars(Fe415/Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 1.5 | 1.5
15 | RCC M- 25 Desgin mix (380 Kg Cement) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including sales & other taxes on all materials excluding Seionarage charges, including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work as directed by Engineer-in-Charge..
i | Footings | 1 Cum |  | 5.25
ii | Columns | 1 Cum |  | 1.15
iii | Piles | 1 RM | 84
iv | Pile caps | 1 Cum | 1.75
v | Plinth Beams | 1 Cum | 4.2 | 4.2
vi | RCC bed block | 1 Cum | 1.85 | 1.85
16 | Construction of Brick Masonrywalls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | 1 Cum | 18.5 | 18.5
17 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Cum | 80 | 80
18 | Supply and keeping the 600 mm dia hume pipe in position including fixing collers etc.complete. | Rmt | 12 | 12 | 12
With RR Masonary wall
19 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | 1 Cum |  |  | 45
20 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P,excluding seionarge charges etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum |  |  | 4.8
21 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | 1 Cum |  |  | 4.8
22 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in- Charge. | 1 Cum |  |  | 90
23 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Cum |  |  | 80
24 | Supply and erection of MS gate made out of MS rods, angles,channels, flats etc. for main entrance gate fixed in to the gate pillars including cost and conveyance of all the materials, fabrication charges,fixing charges, labour charges etc., complete for finished item of work as directed by the Engineer-in-charge. | 1 Kg | 250 | 250 | 250

## Semi Indoor-Sch II
Schedule-II : Electrical works for new 33/11KV Semi -Indoor Sub-station
Sl. No | Description of Item | Unit | Qty. (With 1No 5MVA PTR, 3Nos. Feeders)
1 | Erection of Power Transformer : Loading, Unloading, Erection, and wiring complete as per departmental standards excluding testing and commissioning of 33/11KV 5MVA Power transformer with all accessories like radiators, conservator etc., including RTCC (Remote Tap Changer Control) panels in control room, unloading of power transformers, fixing of radiators, filling of transformer oil complete, to the substation site (With new/retrived 5MVA PTR received directly to Substation site ( including transport) | Each | 1
2 | Supply and Fixing of 105 lb rail poles of 3 Mtr. Length each over the transformer plinth including cost of rail poles, with stoppers. | Each | 2
3 | Supply, loading , unloading and Erection and wiring complete as per departmental standards, testing and commissioning of the following equipment including all incidental handling by skilled, unskilled personnel, T&P bolts and nuts required etc. complete. Any drilling, welding, grouting jobs, slab holes etc. connected with the above works has to be carriedout and the rate quoted is including of all the jobs as per the technical specification. ( including Transport)
i) | Indoor 33KV Air Insulated switchgear for incoming cubicles & transformer incoming cubicles: 33KV, 25KA 1250A Vaccum type indoor AIS switchgear type circuit breakers of APEPDCL approved make for incommers, transformer control cubicles, feeder cubicles complete with aluminium bus bar connectors/control cables, glands, CTs(class 5p10 & 0.2s)& CR Panels with IED relays, bus bars and electrical equipment fitted with electrical wiring, annunciation board with digital 3 1/2 digit ammeter & voltmeter and electronic TVR meter make L&T /Secure with mod bus facility (RS 232 port) and MRI compability with class of accuracy 0.2S and relays of Asidha/ABB/Areva/ L&T/ Siemens/Schneider as per section 5 of technical specification.
(a) | Feeder cubicles with IED relay | Each | 2
(b) | Transformer cubicles with IED relay | Each | 1
(c) | Bus coupler with bus raiser cubicles with IED relay | Each | 1
(d) | Supply and Erection of set of 3Nos 33 KV single phase PTs of ratio 33KV/SQRT(3)/110*SQRT(3) of 0.2 class, Burden 25 VA | Set of 3Nos | 2
ii) | Indoor 11KV switchgear for three outgoing cubicles, one tranformer outgoing cubicles and one for capacitor cubicle 11KV, 25KA 1250A Vacuum type indoor switchgear with drawout type circuit breakers of APEPDCL approved make for transformer control cubicles, feeder cubicles and cubicles complete with aluminium busbar connectors/control cables, glands, CTs & CR Panels with relays (class 0.2s) and electrical equipment fitted with electrical wiring annunciation board with digital 3 1/2 digit ammeter & voltmeter and electronic TVR meter make L&T or Secure with mod bus facility (RS 232 port) and MRI compability with class of accuracy 0.5 and relays ABB/Areva/ L&T/ Siemens as per section 5 of technical specification.
(a) | For feeder cubicles with IED relay | Each | 3
(b) | For Transformer cubicles with IED relay | Each | 1
(c) | For Bus coupler cubicles with IED relay | Each | 1
(d) | 11 KV 3 - Phase PTs of ratio 11 KV/110Volts, Class 0.2, Burden 100 VA | Each | 1
4 | Erection of 3 Phase 25 KVA CSP Station Transformer with accessories complete (Wiring,Earthing) including cost of supply & erection of pole, LT Distribution box,PVC Cabling shall be done from DTR to AC Distribution panel in the control room including transport, loading and unloading charges of all materials. (DTR will be supplied by APEPDCL)
a | Supply,transport and erection of 1No. 9.1M/280 Kg WL PSCC pole for DTR | Each | 1
b | Erection of 3 Phase 25 KVA CSP Station Transformer on pole with Mounting arrangement | Each | 1
c | Supply & Erection of 11KV Isolator 200Amps with single break with single phase arrangement | Each | 1
d | Supply & Erection of 11KV HG fuse set with accessories complete | Each | 1
e | Supply & Erection of LT Distribution box (SMC) size : 900mm (L) X 275mm(B) X 475mm(H) thickness 2 mm minimum for 2 No's Out going feeders including 6 No's 300A 500V knife type porcelain fuse units and red oxide paint | Each | 1
f | HT/LT wiring with PVC Cable 95Sq.mm from Station DTR to LT distribution box to AC distribution Panel in control room including DTR earthing with No.8 GI wire and terminal cable connections with Al.lugs. | Rmt | 45
5 | Power cable for 33KV supply : Supply, making terminations, testing and commissioning of 33KV, 3cx400Sqmm, XLPE armoured cable jointing kits suitable for indoor breakers.
i) | 33KV 3X400Sqmm heat shrinkable cable End Termination Kits suitable for Indoor type. | Each | 5
ii) | 33KV 3X400Sqmm heat shrinkable cable End Termination Kits suitable for Outdoor type. | Each | 5
iii) | 33KV 3X400Sqmm heat shrinkable cable Straight through Termination Kits | Each | 1
6 | Power cable for 11KV supply: Supply, making end terminations, testing and commissioning of 11KV, 3cx185Sqmm, XLPE armoured cable with heat shrinkable cable jointing kits suitable for indoor
i) | 11KV 3X185Sqmm heat shrinkable cable End Termination Kits suitable for Indoor type. | Each | 6
ii) | 11KV 3X185Sqmm heat shrinkable cable End Termination Kits suitable for Outdoor type. | Each | 6
iii) | 11KV 3X185Sqmm heat shrinkable cable Straight through Termination Kits | Each | 1
7 (a) | Excavation of cable trench of width 0.50mts X and 1.20 mtrs depth from road level and filling with sand for 50 mm including seigniorage charges for aying of 33 KV/11 KV XLPE UG Cables wherever required and covering the cable with a sand layer of 250mm above, providing of protective cover of shabed stones (0.3x0.5m) with 2 inch thickness over the sand and backfilling the trench with earth, leveling removing the debris if any excluding laying of 33/11 KV XLPE UG Cables for laying, Commissioning and Testing of 33KV line with 3X400 Sq.mm. UG Cable from 33KV DP structure to Substation | RMtr | 205
7 (b) | Excavation of cable trench of width 0.50mts X and 1.00 mtrs depth from road level and filling with sand for 50 mm including seigniorage charges for laying of 33KV/11 KV XLPE UG Cables wherever required and covering the cable with a sand layer of 250mm above, providing of protective cover of shabed stones (0.3x0.5m) with 2 inch thickness over the sand and backfilling the trench with earth, leveling removing the debris if any excluding laying of 33/11 KV XLPE UG Cables. for laying, Commissioning and Testing of 11KV line with 3X185 Sq.mm. UG Cable from Substation to 11 KV DP structure | RMtr | 100
7 (c) | Laying and testing of 33 KV, 3core, 400 Sq.mm XLPE aluminium UG cable in the Open cable trench as per the specification and cable separation with machine cut bricks horizontally for every 3 meters as directed by the Engineer in Charge. This includes all costs of labour, plant and machinery required for laying,cost of machine cut bricks, warning tapes & laying, transportation of all materials from Stores to work spot, loading and unloading. | Mtr. | 450
7 (d) | Laying and Testing of 185Sq.mm, 11KV, 3Core, XLPE aluminium UG cable in the Open Cable trench as per the specification and separation with machine cut bricks horizontally for every 3 meters as per the specification. This includes the cost of laying of cable, cable warning tapes, cost of machine cut bricks & laying, transportation of all materials from Stores to work spot, loading and unloading. | Mtr. | 300
8 (a) | Supply, laying, testing and commissioning of LT 3 1/2C 50Sq.mm XLPE armoured cable from station transformer to main distribution box should run partly under the ground and partly on tray with proper dressing & clamping including termination on both ends, loading unloading and transport. | Mtr. | 100
8 (b) | Cable terminations to the switchgear, Marshalling boxes /Panel terminal blocks/control & relay panels, LTAC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules and lugs) LT 50Sq mm sqmm cable with copper/Aluminium lugs each core at both ends. | Each | 16
9 | Control cables :
Supply and laying of various sizes of control cables in the cable trenches and the cable should run on cable GI trays (wherever necessary) with covers and proper clamping arrangements and providing of suitable glands and lugs and junction boxes wherever necessary includes loading unloading and transportation.
(a) | 2 Core 2.5Sq.mm copper cable for all breakers from DC distribution box | Mtr. | 400
(b) | 4 Core 2.5 Sq.mm copper cable from battery to DC distribution box | Mtr. | 400
(c) | 10 Core 2.5 Sq.mm Copper cable | Mtr. | 10
(d) | Cable terminations to the switchgear, Marshalling boxes / Panel terminal blocks/ control & relay panels, LTAC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules and lugs) 2.5 sqmm Copper cable with copper lugs each core at both ends. | Each | 150
10 | Supply and erection of ladder type, G.I cable trays for
(a) | Supply and installation transportof 300 mm x 50 mm x 1.6 mm thick GI perforated cable tray without cover along with required angle supports, with coupler plates, Anchor bolts and nut shorizontal and vertical bends, reducers tees,cross members and other accessories as required etc complete and the tray should be fitted on the stone masonary wall by providing hole in the wall wherever necessary and also including necessary masonary work etc. complete for take off arrangement at PTR on HV and LV side as per direction of Emgineer-In-charge | Mtr. | 10
(b) | Supply and installation transport of 450 mm x 50 mm x 2 mm thick GI perforated cable tray without cover along with required angle supports, with coupler plates, Anchor bolts and nut shorizontal and vertical bends, reducers tees,cross members and other accessories as required etc complete and the tray should be fitted on the stone masonary wall by providing hole in the wall wherever necessary and also including necessary masonary work etc. complete for take off arrangement at PTR on HV and LV side as per direction of Emgineer-In-charge | Mtr. | 10
11 | Supply and Erection of Supply and Erection ofLT AC Panel Board with 2/1.6 mm thick MS Sheet 1.2mt lenth/width suitable for fixing 63 Amps and Al bus bar 3ph 4P MCCB (I/C)-63A, 3P-32A MCBs-1, and 6 Nos.2 pole 32 Amps MCBs, Digital Volt meter, Digital Ammeter in powder coating & Led indication lamps, CTs 125/5A at incomimg to MCCB includingmounting on channel including giving all connections as per dirctions of Engineer - in Charge | Each | 1
12 (a) | Excavation of earth pit, putting cast iron pipe with flange on one end (as per ISS 718/74) of nominal dia 150 mm and 2.75 meters long (for PTR neutral and LAs) inside the pit and back filling the pit with bentonite compound and black cotton soil, and filling the earth pit with Bentonite Powder including back filling, cement collar of size 600mm dia and 600 mm height as per departmental standards, including cost of all materials, labour etc. complete. | Each Earth pit | 2
12 (b) | Excavation of earth pit, putting cast iron pipe with flange on one end (as per ISS 718/74) of nominal dia 80 mm and 2.5 meters long (for the balance earth electrodes) inside the pit and back filling the pit with bentonite compound and black cotton soil, and filling the earth pit with Bentonite Powder including back filling, cement collar of size 600mm dia and 600 mm hight as per departmental standards, including cost of all materials, labour etc. complete. | Each earth pit | 8
13 (a) | Connecting of neutral of PTR to earth pit with 2 Nos 75x8mm MS Flat. Run both flats by over laping as one from neutral stud to earth pit and terminating with 2 Nos.flexible copper jumpers of size 50x6 mm 15 inches length including cost of all materials, labour etc. complete on necessary support structure with post type insulators. | RMt | 16
13 (b) | Connecting of earth mat(grid) and connection between earth electrodes and earth grid with 75x8mm MS Flat including cost of all materials, labour etc. complete. | RMt | 300
14 (a) | Supply and erection of Sand Bucket stand with 4 Nos. buckets | Set | 1
14 (b) | Supply and fixing of Co2 type Fire Extinguishers 4.5 Kg capacity confirming to IS 2878 made from ISI marked steam less cylinder confirming to IS:7285 & CE certified and fitted with ISI marked controlled valve confirming to IS:3224, high pressure 1 Mtr discharge hose & horn complete with initial gas charged with carrying handle with wheels and wall mounting bracket. Squeeze lever discharge, used unused indicator, Aphoxy coated paint (Red) with 93% gloss with 2 years warranty Safex / Kenex / Bharat / Reliance/NewTech make) Including transportation, all taxes and all labour charges etc complete.(rate as per R&B SSR 21-22, Item No.610 cat-II), | Each | 3
14 (c) | Supply and fixing of ISI mark (IS:15683) Mono ammonium phosphate powder 90 (MAP) 4 Kg Fire extinguisher, stored pressure type, pressure gauge, gross wt. 6.9 kg, empty wt.2.9 kg, Discharge time minimum 13sec, controllable discharge mechanism, range min. 4 mts applicable on classes A,B, C & electrically started fire, A rating -3 A, B rating -34 B, can construction: Deep drawn and Co2 mig welding, Valve construction: Forging & Machining, internal coating of can: Epoxy powder coating, External coating of Can:Epoxy polyster powder coating, sheet metal thickness:1.60mm, Helium leak detection tested with 5 years warranty Including transportation, all taxes and all labour charges etc complete. | Each | 2
15 (a) | Supply of tools - Standard Tool Box with Taparia make Tools consisting of tools and plant as per Annexure 1 of the Technical specification in section 5 | Set | 1
15 (b) | Earth Discharging rods of 10 feet long for HT/LT lines made out of cane stick in PVC Pipe 32mm dia and 2 mm thick, fully covered, at one end fixed with copper strip of size 25X3 mm of 250mm length by 2 Nos. brass bolts and wing nuts with washers having 6 Sqmm PVC flexible copper wire of 20 Mt length. | Each | 2
16 | Supply and erection of Synthetic Rubber Mats as Per IS 15652 in control room 2.5 mm thick | Sqmtr | 30
17 | Supply & erection of Yard lighting supports including pit excavation and Concreting 0.6x0.6x1.5Mts. with C.C.(1:3:6) using 20 mm and 12mm HBG metal with 8.0Mtrs/200 Kg WL PSCC Poles (Poles are to be supplied by the contractor) includes loading unloading and transportation. | Each | 5
18 | Supply & installation of 60W LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 100 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5/Sec-3), Driver surge protection 4KV, In house additional Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete a) LUMINAIRE MAKE : Wipro(Skyline) / Philips (Green line) / GE-Venture / Crompton(Neo Series) / Bajaj (Edge) / Halonix(Lumos - Super) / Havells (Endura Series) /Capart(Premium)/Greenlites(Hi-Lux) /Polycab/Keselec/ HPL(City Vision)/ Jaquar(Premium)/Eveready/ Surya (Pollux) / FortuneArrt (Leaf) b) LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG by using LT AC cable 2 core 6 Sq.mm, GI Pipe 3/4" dia, MS Clamp set to Hold GI Pipe with Bolt & Nuts, 155 X 210 X 92 Size thermo plastic cable junction boxes with IP66/67 weather proof, for outdoor installation with konckouts for cable entry including terminals etc., complete (sizes in mm) Make : Hensel/Sadhrish, along with 5 Amp Fuse Unit. | Each | 5
19 | Supply and fixing of 125 mm dia 3 mm thick GI Pipe Vertically from bottom to top of DP and laying of 33KV/11KV UG cable through pipes in complete shape for cable take off / tapping arranements | RMt | 25
20 | Supply and erection of line DP structure with poles as per drawing enclosed (fixing of 2Nos 100x50mm MS channel cross arm at top and 2nos 100x50mm MS channel crossarms at bottom & 2nos 65x65x6mm MS angle for brasing with necessary back clamps with 75x8mm MS flat at various locations including supply and erection of 6Nos. 33KV Ploymer disc insulators with hard ware including jumpering providing suitable size alluminium T' clamps (but excluding concreting of poles) including supply and erection of 1 No. CI earth pipe with flange (80mm dia, 2.5Mt long) as per drawing, double earthing should be done for all the structure parts including AB switch with 4mm GI wire and coil earthing is to be done for AB switch handle erection of earth pipe and supply and refiling the earth pit with bentonite compound and black cotton soil (in 1:6 ratio) and giving connections as per departmental standards as per drawing enclosed spun pipe of 2 feet dia. and 2 feet height (cement collar) shall be provided around each earth electrode and all the earth wires should run through 1"dia PVC pipe 3' above the ground level and 2' below the grond level along the pole (wherever alluminium feerules are used, alluminium tape is to be wound over the conductor to have better grip). Line D.P. with A.B.Switch with 12.5Mts Spun poles for 33KV cable incoming AB switch | Each | 1
21 | Supply and erection of line DP structure with poles as per drawing enclosed (fixing of 2Nos 100x50mm MS channel cross arm at top and 2nos 100x50mm MS channel crossarms at bottom & 2nos 65x65x6mm MS angle for brasing with necessary back clamps with 75x8mm MS flat at various locations including supply and erection of 6Nos. 33KV Ploymer disc insulators with hard ware including jumpering providing suitable size alluminium T' clamps (but excluding concreting of poles) including supply and erection of 1 No. CI earth pipe with flange (80mm dia, 2.5Mt long) as per drawing, double earthing should be done for all the structure parts including AB switch with 4mm GI wire and coil earthing is to be done for AB switch handle erection of earth pipe and supply and refiling the earth pit with bentonite compound and black cotton soil (in 1:6 ratio) and giving connections as per departmental standards as per drawing enclosed spun pipe of 2 feet dia. and 2 feet height (cement collar) shall be provided around each earth electrode and all the earth wires should run through 1"dia PVC pipe 3' above the ground level and 2' below the grond level along the pole (wherever alluminium feerules are used, alluminium tape is to be wound over the conductor to have better grip). Line D.P. with A.B.Switch with 11.0Mts Spun poles for 11KV outgoing AB switches | Each | 3
22 | Supply, erection, testing and commissioning of 220V, 80AH sealed, maintenance free battery set with chargers & DCDB and supporting structure complete including supply, erection, testing and commissioning of float/boost chargers suitable for the above batteries with necessary panels as per the technical specification. includes loading unloading and transportation. | Each | 1
23 | Supply and fixing of chequered plates for closing the cable duct including drilling,welding,grouting , holes etc and painting with two coats synthetic enamel paint over a coat of red oxide includes loading unloading and transportation. | Kg | 320
24 | Geotagging of 33/11KV Substation including all equipments details-Locating Co-ordinates(Lattitude & Longitude) using GPS , Collection/Updation of attribute data base of Electrical Network through field survey , development, codification mapping & indexing with their upstream source of supply and Collecting GIS co-ordinates of each asset in Substation , collect attribute information and the SLD approval to be taken from Engineer in Charge for up loading the data. | Nos | 1
25 | Supply and fixing of 2 Nos. earths for each SS with Rail pole 90 lb rail poles of each minimum of 14 mts length ( jointing 2 Nos 7 mts rail poles ) for earthing duly drilling of bore well pneumatic compressor of bore 6 1/2 " dia suitable for 6" , 14Mts length M.S.casing pipe ( 7M each earthing ) including cost of T & P and labour and watering arrangement for improving earth resistance and filling the earth pit with Bentonite Powder including back filling, cement collar of size 600mm dia and 600 mm hight as per departmental standards, including cost of all materials, labour etc. complete. | Set | 1
26 | Supply and Fixing of Danger Notice Board of size 250x200mm for high voltage system, the plate shall be made from mild steel sheet of at least 1.6mm thick and vitreous enameled white, with letters, figures and the conventional skull and cross-bones in signal red colour (refer IS:5-1978) on the front side. The rear side of the plate shall also be enamelled and also the corners of the plate shall be rounded off as per the specification IS:2551-1982 | Each | 2

## OD SS-Sch 1
Schedule-I : Supply and Construction of Control Room etc. for new 33/11KV Outdoor Sub-station
Sl. No. | Description of work | Unit | Quantity
I | Constructions of Control room
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | 1 Cum | 60
2 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) as per Directions of Eng-in-Charge. | 1 Cum | 50
3 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including, excluding Seionarage charges, conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310)as per Directions of Eng-in- Charge. | 1 Cum | 25
4 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | 1 Cum | 10
5 | Providing HYSD/TMT/MS Steel bars (Fe415/ Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 1.6
6 | Providing Antitermite treatment as per IS 6315 (Part - 2) 2001 (Pre-constructional chemical treatment measures) along the internal & external vertical faces of the columns, plinth beams, basement and top surface of the basement filling below flooring bed as per the specified procedure conforming to IS 6315 (Part-2) 2001 and other relevant approved specification duly using Chlorpyriphos/ Lindane emulsifiable concentrate 20% with 1% concentration @ 7.5 Liters/ sqm of the vertical surface & @ 5.0 Liters/ sqm of the horizontal surface of the substructure to a depth of 500 mm around columns & 300 mm deep around plinth beams, basements & floor filling area including excavation channel along the wall & rodding etc & cost & conveyance of all materials to the site, cost of labour for spraying, rodding etc complete for finished item of work as per the approval of the Engineer-in-Charge | 1 Sqm | 40
7 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in-Charge. | 1 Cum | 35
8 | Construction of Brick masonry walls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | 1 Cum | 25
9 | 11.5 cm wide Brick masonry for super-structure on ground floor in cm (1:3) using second class traditional size bricks including cost of all materials and it's conveyance, labour and all operations for constructing half brick masonry, mixing cement mortar, curing etc.,complete. at locations given below, excluding Seionarage charges: | 1 Cum | 5
10 | Filling of gravel in trenches, sicks of foundations, basements etc. of approved quality in layers not exceeding 15 c.m. thick consolidating each deposited layer by watering and ramming including cost and conveyance of gravel ,excluding seignoirage charges, water to work site and operational, incidental, labour charges etc. complete for furnished item of work | 1 Cum | 25
11 | RCC M- 25 Desgin mix (380 Kg Cement) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including sales & other taxes on all materials excluding Seionarage charges, including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work as directed by Engineer-in- Charge..
i | Footings | 1 Cum | 4.5
ii | Plinth beams | 1 Cum | 2
iii | Lintel beams | 1 Cum | 1.5
iv | Columns | 1 Cum | 2
v | Piles | 1 RM | 40
vi | Pile caps | 1 Cum | 2
vii | Sunshades and Chajjas | 1 Sqm | 10
viii | Roof beams | 1 Cum | 2.2
ix | Roof Slab | 1 Cum | 4.75
12 | Providing R.C.C. racks of 38mm thick with R.C.C.(1:2:4) and plastering with CM(1:3),12mm thick excluding seigniorage cost and conveyance of all materials to site and all labour charges complete excluding seionarage charges and as directed by the Engineer in charge.. | 1 Sqm | 10
13 | Construction of cable duct in the control room shall be of size 300 x 300mm with PCC 1:4:8 using 40mm metal 100mm thick and 115mm thick brick masonry on 2 sides and Plastering 3 sides with CM 1:5 closing of duct with cement slabs of 50mm - thick using RCC 1:2:4 using 10mm HBG metal includes cost of all materials and labour and the cost of cement excluding seionarge charges (as per Technical specification) | RMt | 5
14 | Supply and keeping the 300 mm dia hume pipe in position including fixing collers etc.complete. For Running of Control Cables, XLPE Cable etc from Switch yard to Control Room, including excavation and backfilling etc | Rmt | 5
15 | Providing impervious coat to exposed RCC roof slab surface with CM(1:3), 20mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying, rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc,, complete for finished item of work excluding Seionarage charges for finished item of work as directed by Engineer-in- Charge.. . | 1 Sqm | 45
16 | Plastering to ceiling 12 mm thick in one coat in CM(1:3) with Smooth finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves excluding seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 40
17 | Plastering 12 mm thick in one coat for superstructurefor even faces of walls with CM(1:5) with smooth finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves, excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge | 1 Sqm | 120
18 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 170
19 | Flooring with a bed of 100mm thick in CC (1:4:8) with 40mm & 20mm size HBG Metal from approved quarry including cost and conveyance charges of cement and all other materials to site, seigniorage charges, labour charges for machine mixing, laying concrete, finishing top surface to the required level, curing etc., complete for finished item of work | 1 Cum | 6
20 | Flooring with vitrified polished floor tiles glossy finish premium colours of size not less than 598x598mmx8mm thickness of 1st quality(make Somany,HR Jhonson,Naveen Ceramics, Kajaria, Nitco, Sphinx) set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand water and tiles etc., complete, complete for finished item of work including the cost of conveyance of all materials excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 30
21 | Providing skirting to internal walls to 10 cm height/risers of steps vitrified polished floor tiles glossy finish premium colours of size not less than 598x598mmx8mm thickness of 1st quality(make Somany,HR Jhonson,Naveen Ceramics, Kajaria, Nitco, Sphinx) set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand water and tiles etc., complete, complete for finished item of work including the cost of conveyance of all materials excluding Seionarage charges etc., complete for finished item of work and as directed by the Engineer in charge. . | 1 Sqm | 4
22 | Flooring with Non-skid red or white full body Ceramic floor tiles of size 300 x 300 mm and thickness between 7-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs set over base coat of cement mortar (1:8), 12 mm thick over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3.kgs per sqm & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, potable water, sand and tiles etc., complete for finished item of work. | 1 Sqm | 15
23 | Dadooing in toilets and bath rooms with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs set over a base coat of CM (1:3) 12 mm thick with neat cement slurry of honey like consistency spread at the rate of 3.3 Kgs per Sqm and filling the joints with white cement paste mixed with pigment of matching shade is to be done including cost and conveyance charges of cement, potable water and all other materials to site, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 10
24 | Painting with Interior grade synthetic polymer plastic emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/ litre of approved brand and shade two coats over a base coat of appropriate interior primer(grade-I) of Asian make, making 3 coats in all to give an even shade after thorughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and convyance of all materials, labour charges and incidental charges such as scaffolding, lift charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 120
25 | Painting with acrylic exterior emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/ litre exterior grade of approved brand and colour/shade two coats over a base coat of appropriate primer (grade-I) of Asain make , making 3 coats in all to give an even shade after thorughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and convyance of all materials, labour charges and incidental charges such as scaffolding, lift charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 170
26 | Supply and fixing of doors with well seasaned country wood frames 3" x 4" ( 1H.2V ) (sal wood / Kamba wood ) of the required sizes as given in drawing using 35mm thick flush door shutters solid bond wood block board type with commercial ply on both sides and both the surfaces are decorated with 1.5mm thick laminate sheets glossy finish and polishing the frame and with aluminium accessories like aldrops, hinges, door handles, door stopper etc.,including painting two coats with synthetic enamel paint over coat of wood primer with putty including cost of wood and all materials to site and all labour charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Sqm | 2.75
27 | Supply & fixing of windows with well seasoned country wood with outer and centre frame size 3" x 4" ( Sal wood / Kamba wood ) with hold fasts with two shutters with 5mm thick pinheaded glass panels including cost of wood, cost of making charges and fixing iron grills of approved design with 9mm size square rod and aluminium accessories like window stay, tower bolts, hinges etc., including painting two coats with synthetic enamel paint over coat of wood primer with putty including cost and conveyance of materials, labour charges, hard ware, fixing etc., complete for finished item of work and as directed by the Engineer in charge. | 1 RM | 5
28 | Supply and Fixing of 25mm dia 2mm thick P.V.C. pipe (ISI MARK) concealed in reinforcement and walls with all required accessories including masonary work for light, fan and separate plug point including all labour charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 RM | 50
29 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular switch, Ceiling rose and hot dip galvanized metal boxes with cover frame to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings (makes Anchor / Gold Medal / Million / Vimal / Maru / Milltec.) as directed by the Engineer in charge. | Each | 25
30 | Wiring with 2 runs of 14/0.3mm (1.0 Sq.mm) Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular switch and 3/2 pin socket hot dip galvanized metal boxes with cover frame to switch control box including all labour charges etc., complete for light, bell, fan and exhaust fan points in Non-Residential Buildings (makes Anchor / Gold Medal / Million / Vimal / Maru / Milltec.) as directed by the Engineer in charge. | Each | 3
31 | Wiring with 2 of 22/0.3mm (1.5 Sq.mm)P.V.C. insulated F.R. flexible copper cable (ISI MARK) in existing pipe with 16A modular switch control and 3 pin/16A sockets with hot dip galvanized box with cover frame on separate board including all labour charges etc., complete. | Each | 1
32 | Supply and run of 2 of 22/0.3mm (1.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for MAINS Makes: Finolex / RR kabel / Havells/ KEI/Polycab/Gloster /Goldmedal/ GM inlcuding all labour charges etc., complete. | 1 RM | 100
33 | Supply and run of 1 of 22/0.3mm (1.5 Sq.mm) F.R P.V.C. insulated flexible copper cable in existing pipe for earthing Makes: Finolex / RR kabel /Havells/KEI/Polycab/ Gloster /Goldmedal/ GM inlcuding all labour charges etc., complete. | 1 RM | 100
34 | Supply and fixing of 8way TPN Distribution board with IP-20 protection suitable for 3 phase ELCB / RCCB / FP with 40A, 4pole isolator as incomer and 10kA-6-32A (12Nos) SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc., complete as directed by the Engineer in charge. | Each | 1
35 | Supply and fixing of 18W/20W, 1200mm length LED( with LED light) batten light with extruded alluminium housing and polycarbonate cover, input voltage AC 220 - 260 Volts with PF>0.9, Surge protection: 2KV,THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 5700K, minimum CRI>70, .etc., complete. a) LUMINAIRE MAKE : Phillips / GE-Venture / Crompton / Wipro / Bajaj / Havells / Halonix/Jaquar/ HPL/GM / GreenLites / Gold Medal/ Eveready b) LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG/ Everlight as per directions of Eng-in-Charge. | Each | 4
36 | S&F of 9W LED Lamps with Holder of standard make including cost of all fixture etc., complete as per directions of Eng-in-Charge. | Each | 4
37 | Supply and fixing 48" (1200mm) Sweep Ceiling Fan of makes (Crompton High speed/Bajaj Ultima/Havells Velocity/ Usha Astra/ Orient Summer Pride) with Modular Electronic Regulator of makes (Crab Tree/Feno Swtch/ Toyoma/Fortune Art/ Million / Gold Medal / Vimal / Anchor Roma) as directed by the Engineer in charge. | Each | 3
38 | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of size with encapsulation of 8MM rigid layer on all the six surfaces. The door frame will have a rebat of 32MM. Door Frame section of 63.5x100 MM .The two Vertical members are to be joined together with the horizontal member using 8x75 MM long MS Star full thread screws to be used with reverse forward speed control hand drilling machine. The ready/assembled door frame is fixed to the wall using hold fast or bolt fasteners. A minimum of 4 No.s of screws to be provided for each vertical member & minimum 2no.s for horizontal member.
a | Door Frame section of 63.5x100 MM .The two Vertical members are to be joined together with the horizontal member using 8x75MM long MS Star full thread screws etc., rate vide item code BMT-N.83.C | 1 RM | 1.5
b | Providing and fixing 28 -30 MM thick solid Wood Polymer Composite(WPC) single extruded door shutter with 3MM top and bottom rigid layer with an overall density of 750kg/Cum. It will be fixed to the frame using 3 inch /4 inch hinges. A minimum of 4 hinges will be required for fixing the door with the frame including labour charges, 4Nos 125mm aluminium butt hinges, 1No 250mm aluminium aldrop, 1No 200mm aluminium tower bolt, 2Nos 150mm aluminium handles etc., complete for finished item of work as directed by the Engineer in charge. | 1 Sqm | 2
39 | Supply and fixing of European Water Closet of Ist quality with plastic seat and lid and PVC flushing tank 10 Lit capacity confirming to IS:2556-Part-2-1973 of Hidustan/Neycer or Parry ware make white glazed with 'S' trap including all materials ,labour etc complete as per directions of Eng-in-Charge. | Set | 1
40 | Supply and fixing 550 x 400mm size Indian make Flat Back Wash Hand basin with pedestal (HSW/Parryware/Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15mm nominal bore chromium plated pillar tap of 1st quality Indian make 400 grams Seiko/Senior/Nice/Esso or equivalent complete with standard CI brackets : 550 x 400 mm - double C.P. Pillar cock etc complete as directed by the Engineer in charge. | Set | 1
41 | Supply and fixing 450 x 300 mm Belgium glass 6mm thick frameless mirror with stand mounted to wall including plugs and screws as directed by the Engineer in charge. | RMt | 1
42 | Supply and fixing of Unplasticised PVC Pipes,10 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color including Labour charges for laying, fixing, and commissioning the pipes including couplers, bends, plugs, junctions, tees etc. with solvent jointing as per Standard practice for finished item work as directed by the Engineer-in-charge.
a | 25 mm dia | RMt | 40
b | 20mm dia | RMt | 20
43 | Supply and fixing of CP Long body bib cock fancy type delux heavy duty 12.7mm dia Indian make 400gm seiko or equivalent etc., complete for finished item of work as directed by the Engineer - In - Charge | Each | 2
44 | Supply and fixing of dia (4kg/sqcm) PVC pipes of make Prince/Sudhakar/Kisan/Supreme or any ISI Brand including bends, Tees etc., including cost and conveyance of all materials all labour charges etc., complete. as directed by the Engineer in charge.
a | 75 mm dia | RMt | 5
b | 110 mm dia | RMt | 20
45 | Constructing 2’ x 2' brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 /sq.mmincluding plastering with cement mortar 1:3 prop; ½” thick both inside and outside fitted with 20” dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc. to site, and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification excluding Seionarage charges as directed by the Engineer in charge. | Each | 1
46 | Providing of pheripheral fencing arround the site as given in the drawing including cost of R.C.C. fencing poles, G.I. barbed wire & stringing etc., complete for finished item of work. (excluding cost of excavation of pits & concreting)
a | Supply,placing in alignment of RCC fencing post of 1.8m length including cost and conveyance of fencing post, labour charges for placing in alignment all are as specified by the Engineer-in-charge at site - - etc., complete. | Each | 60
b | Supply and fixing galvanised steel barbed wire (IS:278-1962 Type I) weighing 9.36kg per 100 mtrs (min), Straining and fixing to any type of standard, including securing galvanised mild steel wire etc., as directed by engineer - in - charge | RMt | 1200
II | Erection of Control Equipment and Accessories in Control Room
47 | Supply & Erection, and wiring complete as per departmental standards excluding testing and commissioning of the following equipment of LTAC panels, annunciation panels in the control room, duly mounting them on channels and grouting them with foundation bolts including cost of cable laying in the trench of size 300 x 300 mm
a | LTAC panel (as per Section 5) in the Control Room on Cable Duct with necessary Channel Supports | Each | 1
b | DC Annunciation Board (as per section 5) with Hylam sheet of 8mm thickness (on M.S.Angle stand of 1.25x1.25 M, & height 1.25M (M.S.angle 50 x 50 X 6 mm) with 33KV & 11KV Bus PT Volt Meter (Voltmeter shall have selection option to read all the three phase voltages).With multi tone electronic hooter (24 Volts DC), indicators and Push Type Switches in the Control Room on Cable Duct with necessary Channel Supports | Each | 1
c | RTCC (Remote Tap Changer Control) Pane, wiring complete duly mounting on Channels in the Control Room. (RTCC panel will be supplied along with PTR) | Each | 1
48 | Providing independent earthing by excavating a trench to a depth of 2.7 M in all soils, as per size specified in the Data, using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of Salt and Charcoal in layers and all labour charges etc., complete for small quarters. | Each | 2
49 | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete. | Each | 10
50 | Supply of steel office Table of size 4' x 2' x 30" with 18 mm plywood , Teakwood finishing with Drawers on right hand side and with automatic locking system(Godrej or equivalent make)as directed by engineer - in - charge. | Each | 1
51 | Supply of chairs with arms teak wood Frame 1" thick,seat & backs, 's' type in 1" dia pipe(Godrej or equivalent make)as directed by engineer - in - charge. | 1 Sqm | 2
52 | Supply of Quartz wall clock 1' x 1'size of reputed make. | Each | 1
53 | Writing Name of the SS in Details on the Control room one side as directed by the Engineer in charge. | Each | 1
54 | Writing Name of the SS in Details on the Gate as directed by the Engineer in charge. | Each | 1

## OD SS-Sch II
Schedule-II(A) : Supply and Construction of Switchyard CIVIL at 33/11KV Outdoor Sub-station
Sl. No. | Description of work | Unit | Quantity
I | Civil Works for Switch Yard
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | CUM | 95
2 | Laying foundations for main and auxiliary structures, supports, breaker and transformer plinths, coping of supports etc., shoring, shuttering, and dewatering the pits before and during the process of laying concrete in following proportions and curing for 14 days including concreting of beam upto mother soil as per the direction of the Engineer incharge certified by Quality Control and Civil drawings (Rate quoted shall be inclusive of fixing and concreting foundation bolts wherever necessary excluding seionarage cahrges) (Sketches enclosed) (as per Technical specification)
a | a. Cement concrete 1:3:6 using 12 to 20 mm H.B.G.metal | CUM | 13
b | b.Cement concrete 1:3:6 using 20 to 40 mm H.B.G.metal | CUM | 127
3 | Plastering the foundation plinths with 12mm thick in 1:3 cement mortar and white washing (two coats) with White Cement or equivalent cement paint, including cost of all materials and cement excluding seionarge charges. | Sq.M | 160
4 | Supply and Fixing of 105 lb rail poles of 3 Mtr. Length each over the transformer plinth including cost of rail poles, with stoppers. | Each | 2
5 | Excavation of cable trench of size 300 x 300 mm in the switch yard including cost of all materials and labour complete(as per Technical specification) for laying of LT Cable from DTR to Control Room | RMt | 70
6 | Construction of security wall on the existing R.R retaining wall/Brick Masonary wall including providing P.C.C 1:2:4 with 20mm HBG metal of 50 mm thick and construction of Brick Masonary wall of CM 1:6 for about 300mm height all over the security fencing and construction of brick pillers of size 230 mm X 230mm for fixing of jally 900mm X 600 mm size and providing RCC plates of width 230mm and thickness 50mm over the jally and brick pillers properly and plastering the entire portion with Cm 1:5 20mm thick and white washing the area with two coats including cost of all materials, labour etc complete excluding seionarage charges for finished item of work as per dawing as per directions of Eng-in-charge. | RMt | 105
7 | Supply and spreading of quarry dust to a thickness of 25mm, excluding seigniorage (after consolidation of the earth work with a roller.) | CUM | 20
8 | Supply and spreading of 20mm size machine crushed blue granite metal to a thickness of 75 mm over spread quarry dust excluding seigniorage. | CUM | 50
II | Providing of Pipe Line for Earth Pits in the Switch Yard, minimum 2 Sections to be made in Switch Yard using Gate Valves
1 | Supply and fixing of different dia.Unplasticised PVC Pipes,10 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (third revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color including Labour charges for laying, fixing, and commissioning the pipes including couplers, bends, plugs, junctions, tees etc. with solvent jointing as per Standard practice for finished item work as directed by the Engineer-in-charge.
a | 32mm dia UPVC pipe | 1 RM | 120
b | 25mm dia UPVC pipe | 1 RM | 145
c | 20mm dia UPVC pipe | 1 RM | 40
2 | Supply and fixing CP Short body bib cock facy type deluxe heavy duty 12.7mm dia Indian make Seiko/Senior/Nice or equivalent | Each | 30
3 | Supply and fixing of GM Gate ( GM peet) valves as per IS 778 Class I -Indian make heavy type of different sizes including cost and conveyance of all materials and labour Charges complete for finished item work as directed by the Engineer-in-charge.
a | 32 mm GM Gate valve | Each | 1
b | 25 mm GM Gate valve | Each | 2
c | Electrical Works
III | Electrical Works
1 | Supply, fabrication, welding & erection of structural supports (BF beams 150x150 mm & drilling holes with machine) each 8/8.5/9.0Mtrs in length (As per the directions of the Engineer-In-charge), Structural Members (M.S.Channel 100 x 50mm, MS angle 65X65X6 mm) and seating channels including bolts & Nuts for BF beams & MS Channel as per section-5 and as per relevant Indian standard | MT | 15.5
2 | Formation of 33KV & 11KV strung bus with single 200Sq.mm Panther AAAC/ACSR conductor for each phase including hoisting of insulators and hardware, stretching, measuring, cutting, stringing, tensioning, clamping of the conductor, fixing of post type insulator to support the conductor wherever necessary and fixing of disc insulators including cost of all materials, conveyance, labour and with all leads for substation with single power transformer as per Technical Specification in complete shape (For Two PTR with 4 feeders with 33KV Auxillary bus) | Each | 1
3 | Connecting the equipment to bus and for another equipment with single 200sq.mm Panther AAAC/ACSR conductor including measuring, Cutting, Clamping and also fixing of post type insulators assembly to support the conductor wherever necessary including cost of all materials, conveyance, labour and with all leads for substation | Each | 207
4 | Connecting the equipment to bus and for another equipment with single 100 Sq.mm AAAC, including measuring, Cutting, Clamping and also fixing of post type insulators assembly to support the conductor wherever necessary including cost of all materials, conveyance, labour and with all leads for substation | Each | 30
5 | Earthing Connecting Body of Equipment, Structures to Earthpits/Earthmat with MS Flat (raisers) specified. All the Raisers should be provided with Jute beading over a Coat of keeltar. Another Coat of Keeltar should be provided over the Jute Beading as per Technical Specification including Cost of all materials, Lablour etc. Complete
a | With 50x6mm MS flat ( for all raisers from body of Equipment to Grid). | RMT | 800
b | With 2nos. 75 x 8mm MS Flat for neutral of PTR to earth pit are to be Run, both flats by over laping as one end to neutral stud terminating with 2 Nos.flexible copper jumpers of size 50x6 mm 15 inches length, other to earth pit/Grid and to Run the MS Flats on 100x50MS Channel support structure with post type insulators. | RMT | 8
c | With 75x8mm MS Flat (for Grid) | RMT | 445
6 | Excavation of Earth Pit, Putting Earth Pipe (Cast Iron / Galvanized Iron) with Flange on One End (as per ISS 718/74) inside the Pit i.e. 200mm below the Ground Level and Back filling the Pit with Bentonite Compound and Black Cotton Soil in 1:4 Ratio and Providing Cement Collar of Size 600mm Dia and 600mm Height as per Departmental Standards, including cost of all Materials, labour etc Complete
a | CI Earth Pipe of nominal dia 150 mm and 2.75 meters long (for PTR neutral and 33KV Station Type LAs) | Each Earth pit | 2
b | CI Earth Pipe of nominal dia 80 mm and 2.5 meters long (for the balance earth electrodes) | Each earth pit | 24
c | GI earth pipe of nominal dia 40 mm and 2.5 meters long complete without connecting to the Earth Mat (i.e. Grid) for maintaining the independent earth during issuing LCs on the Feeders and also for Battery Chargers Body Earthing | Each earth pit | 8
7 | Supply pavingout and Laying of control cables of all sizes in the excavated cable trench and Cable terminations to the Switchgear marshalling boxes/panel terminal blocks/ control & relay panels, LTAC panel, including providing suitable ferrules and lugs on both ends of each core as per specification (including cost of Ferrules and lugs and glands and labour complete as per technical specification). Note: This includes transportation of cables, running cables in control room, SWITCH YARD and Road crossing etc.,
a | 2Core 2.5 sq.mm.unarmored multi stranded Copper cable | RMT | 200
b | 4 Core 2.5 sq.mm.unarmored multi stranded Copper cable | RMT | 500
c | 10 Core 2.5 sq.mm.unarmored multi stranded Copper cable | RMT | 120
8 | Painting of MS structure supports, and members two coats of 1st class red oxide paint with two coats of Aluminium paint of Asian/Nerolac/ Berger make as per Technical specification including cost of paint and accessories | SQM | 645
9 | Painting of operating rods of 33 KV, 11KV AB Switches with postal Red colour including cost of paint and accessories | Each | 16
10 | Painting of all supports for a height of 0.3 M above the coping with bitumen paint (Black colour) and painting of coping with two coats of white cement (Janatha cement) including cost of paint and accessories | Each | 24
11 | Supply & erection of Yard lighting supports including pit excavation and Concreting 0.6x0.6x1.5Mts. with C.C.(1:3:6) using 20 mm and 12mm HBG metal with 8.0Mtrs/200 Kg WL PSCC Poles (Poles are to be supplied by the contractor) | Each | 8
12 | Supply & installation of 60W LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 100 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5/Sec-3), Driver surge protection 4KV, In house additional Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete a) LUMINAIRE MAKE : Wipro(Skyline) / Philips (Green line) / GE-Venture / Crompton(Neo Series) / Bajaj (Edge) / Halonix(Lumos - Super) / Havells (Endura Series) /Capart(Premium)/Greenlites(Hi-Lux) /Polycab/Keselec/ HPL(City Vision)/ Jaquar(Premium)/Eveready/ Surya (Pollux) / FortuneArrt (Leaf) b) LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG by using LT AC cable 2 core 6 Sq.mm, GI Pipe 3/4" dia, MS Clamp set to Hold GI Pipe with Bolt & Nuts, 155 X 210 X 92 Size thermo plastic cable junction boxes with IP66/67 weather proof, for outdoor installation with konckouts for cable entry including terminals etc., complete (sizes in mm) Make : Hensel/Sadhrish, along with 5 Amp Fuse Unit. | Each | 8
13 | Erection and Wiring Complete as per Departmental Standards excluding testing and Commissioning of the Following equipment including cost of Transport, Labour, handling Charges etc (as per Section 5)
a | 11KV Circuit Breakers with C.T's (feeder) and control panel with HTTVR meter of Class 0.2S, with DLMS protocol, MRI / Laptop Compatibility. | Each | 4
b | 11KV Circuit Breakers with C.T's (LV) and control panel with HTTVR meter , of Class 0.2S, with DLMS protocol, MRI/ Laptop Compatibility ( With / without Differential Protection) | Each | 1
c | 33KV Circuit Breakers with C.T's (feeder) and control panel with HTTVR meter of Class 0.2S, with DLMS protocol, MRI / Laptop Compatibility.(With/without Differential Protection | Each | 1
14 | Supply, Erection and wiring complete for Potential Transformers as per departmental standards excluding testing and commissioning of the following equipment including cost of transport, labour, incidental handling charges etc. (as per section 5)
a | 33 KV, 100VA, class:0.2 Potential Transformer (single phase) set consists of 3Nos | Set | 1
b | 11 KV, 100VA, class:0.2 Potential transformer cubicle (3 Phase type) | Each | 1
15 | Supply, Erection and wiring complete as per departmental standards excluding testing and commissioning of 24 V, 40AH Battery Charger with batteries including cost of all materials | Each | 6
16 | Supply as per specifications and erection and wiring complete as per departmental standards for Lightning Arresters excluding testing and commissioning of the following equipment including cost of all materials, transport, labour, incidental handling charges etc. (as per section 5)
a | 30 KV Lightning Arrestor (Station type) | Each | 3
b | 30 KV Lightning Arrestor (Line type) | Each | 6
c | 9 KV 10 KA lighting arrester (Station Type) | Each | 3
d | 9 KV 5 KA lighting arrester (Line Type) | Each | 12
17 | Supply as per specifications and erection, and wiring complete as per departmental standards excluding testing and commissioning of the following equipment including cost of all materials, transport, labour, incidental handling charges etc. (as per section 5)
a | 33 KV Isolators (800 A) double break, horizontal (Pipe type) | Each | 3
b | 11KV Isolators (800A) with centrally operated, horizontal (LV) double break (Pipe type), Bus Coupler | Each | 1
c | 11KV Isolators (400A) centrally operated horizontal double break for feeders (Knife type) | Each | 8
d | 33 KV HG Fuse Set with accessories complete with Copper Flat 25 x 3mm Size for Horns | Each | 1
18 | Erection and wiring complete as per departmental standards excluding testing and commissioning of 3-Ph, 11KV/415V, 25KVA Station Transformer and supply and erection of 11 KV HG Fuse Set, 11KV AB Switch, A type Distribution box with 2 feeders, including supply and erection of LT knife type fuse units with insulated handle running of earths complete with cost of all material. DTR to be Mounted on already erected Sitting channels (100X50mm), already Provided MS angles (50 X 50 X 6 mm) as belting supports and existing Flat earthing for Body and existing Flat Earthing for Neutral of DTR as per departmental standards. | Each | 1
19 | Unloading, Erection, and wiring complete as per departmental standards excluding testing and commissioning of 33/11KV 5MVA Power transformer with all accessories like radiators, conservator etc., including unloading of RTCC (Remote Tap Changer Control) panels, unloading of power transformers, fixing of radiators, filling of transformer oil complete, to the substation site (With new/retrived 5MVA PTR received directly to Substation site) | Each | 1
20 a) | Supply & Erection, and wiring complete as per departmental standards excluding testing and commissioning of the following equipment of LTAC panels, annunciation panels in the control room, duly mounting them on channels and grouting them with foundation bolts including cost of cable laying in the trench of size 300 x 300 mm - LT AC Cable 25/50 Sq.mm 3 1/2 Core | RMT | 60
b) | Supply and erection of LTAC panel (as per Section 5) | Each | 1
c) | Supply and erection DC Annunciation Board (as per section 5) with Hylam sheet of 8mm thickness (on M.S.Angle stand of 1.25x1.25 M, & height 1.25M (M.S.angle 50 x 50 X 6 mm) with 33KV & 11KV Bus PT Volt Meter (Voltmeter shall have selection option to read all the three phase voltages).With multi tone electronic hooter (24 Volts DC), indicators and Push Type Switches | Each | 1
21 | Supply and erection of marshalling Box on the structure (pole mounted type). | Each | 3
22 | Supply and Erection of Fire Fighting Equipment of the Following
a | Sand Bucket stand with 4 Nos. buckets | Set | 1
b | CO2 Cylinder 4 Nos of 5 Kgs supply and fixing of CO2 type fire extinguishers capacity confirming to IS 2878 made from ISI mark (1 set) | Set | 1
c | ISI mark (IS:15683) Mono ammonium phosphate powder 90 (MAP) 2 Kg Fire extinguisher, stored pressure type, pressure gauge, gross wt. 3.6 kg, empty wt.1.6 kg, Discharge time minimum 8 sec, controllable discharge mechanism, range min. 2 mts applicable on classes A,B, C & electrically started fire, A rating -2 A, B rating -21 B, can construction: Deep drawn and Co2 mig welding, Valve construction: Forging & Machining, internal coating of can: Epoxy powder coating, External coating of Can:Epoxy polyster powder coating, sheet metal thickness:1.60mm, Helium leak detection tested with 5 years warranty Including transportation, all taxes and all labour charges etc complete. Makes : Safex / Kenex / Bharat / Reliance/NewTech | Set | 1
23(a) | Supply of tools - Standard Tool Box with Taparia make Tools consisting of tools and plant as per Annexure 1 of the Technical specification in section 5 | Each | 1
23(b) | Earth Discharging rods of 10 feet long for HT/LT lines made out of cane stick in PVC Pipe 32mm dia and 2 mm thick, fully covered, at one end fixed with copper strip of size 25X3 mm of 250mm length by 2 Nos. brass bolts and wing nuts with washers having 6 Sqmm PVC flexible copper wire of 20 Mt length.
24 | Supply and Erection of 11 KV 2 MVAR Capacitor banks with associated equipment (Normal) Type A (incl Capacitor bank, Equipment Structure, Capacitor Switch, VCB, LA, RVT, C&R panel & Earthing Material) incl Civil, Erection, testing & Commissioning of complete Capacitor bank | Each | 1
25 | Geotagging of 33/11KV Substation including all equipments details-Locating Co-ordinates(Lattitude & Longitude) using GPS , Collection/Updation of attribute data base of Electrical Network through field survey , development, codification mapping & indexing with their upstream source of supply and Collecting GIS co-ordinates of each asset in Substation , collect attribute information and the SLD approval to be taken from Engineer in Charge for up loading the data. | Each | 1

## OD SS-Sch III
Schedule-III : Supply and Construction of Approach Road, Retaining Wall, Levelling of Site etc. for new 33/11KV Outdoor Sub-station
Sl. No. | Description of work | Unit | Retaining wall with pile foundation | Retaining wall with Column foundation | Retaing wall with RR Masonary
I | Construction of Approach road, Reaining wall, Levelling of site etc.
1 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 700 | 700 | 700
2 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310)as per directions of Eng-in-Charge. | Cum | 100 | 100 | 100
II | Formation of WBP Approach road:
1 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 200 | 200 | 200
2 | Providing, laying, spreading and compacting stone aggregates of 65 mm Single nominal size to water bound macadam specification including spreading in uniform thickness, hand packing, rolling with three wheel 80-100 kN roller in stages to proper grade and camber, applying and brooming, crushable screening to fill-up the interstices of coarse aggregate, watering and compacting to the required density as per Technical Specification of MORDto a compacted thickness of 100 mm excluding seionrage charges etc. complete for finished item of work as directed by Engineer-in-charge. | Cum | 60 | 60 | 60
III | Construction of hume pipe culvert:
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | Cum | 17 | 17 | 17
2 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P ,excluding seionarge charges etc., complete for finished item of work. (APSS NO. 309 & 310) etc. complete for finished item of work as directed by Engineer-in-charge. | Cum | 3 | 3 | 3
3 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | Cum | 3 | 3 | 3
4 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in- Charge. | Cum | 10 | 10 | 10
5 | Construction of Brick Masonrywalls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | Cum | 8 | 8 | 8
6 | Supply and filling of borrowed/naturally occuring good gravel in uniform layers and compacting with smooth wheel roller of 10t capacity to achieve the desired density, watering and compacting to the required density as per Technical Specification of MORD including cost and conveyance of all materials,all incidental and operational charges,hire charges of T&P etc. excluding seionrage charges etccomplete for finished item of work as directed by Engineer-in-charge. | Cum | 30 | 30 | 30
7 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | Sq. M | 30 | 30 | 30
8 | Supply and keeping the 600 mm dia hume pipe in position including fixing collers etc.complete as per directions of Eng-in-Charge. | Rmt | 12 | 12 | 12
IV | Construction of Retaining wall around Switch yard:
With Pile foundation / Column Footings
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | Cum | 45 | 45
2 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | Cum | 6.3 | 6.3
3 | Providing HYSD/TMT/MS Steel bars(Fe415/Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 2.2 | 2.2
4 | RCC M- 25 Desgin mix (380 Kg Cement) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including sales & other taxes on all materials excluding Seionarage charges, including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work as directed by Engineer-in-Charge..
i | Footings | 1 Cum |  | 5.6
ii | Columns | 1 Cum |  | 1.9
iii | Piles | 1 RM | 114
iv | Pile caps | 1 Cum | 2.3
v | Plinth Beams | 1 Cum | 5.75 | 5.75
vi | RCC bed block | 1 Cum | 3.75 | 3.75
5 | Construction of Brick Masonrywalls in super structure in CM 1:6 using well burnt country bricks with compressive strength not less than 35 Kg/Sqm from approved source including cost and conveyance of all materials all labour charges etc.excluding Seionarage charges , complete for finished item of work as directed by the Engineer-in Charge. | 1 Cum | 25 | 25
6 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Cum | 110 | 110
With RR Masonary wall
1 | Earth work excavation in all types of soil which can be excavated with pick axes and crow bars and do not require blasting in all conditions such as dry, wet, slushy etc., upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including shoring, strutting and dewatering where ever necessary covering initial lead for foundations for finished item of work. etc as per SS - 20 B (APSS 308) as per Directions of Eng-in-Charge. | 1 Cum |  |  | 90
2 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P,excluding seionarge charges etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum |  |  | 6.5
3 | Plain Cement concrete (1:4:8) using 40 mm HBG metal machine mixed laid in positions in layers not exceeding 15 Cm thickness including cost and conveyance of all materials, , water to work site and all operational, incidental, labour charges such as machine mixing of concrete laying, tamping, curing etc., complete for finished item as per Direction sof Eng-in Charge | 1 Cum |  |  | 6.5
4 | RR Masonry in CM (1:6) cost and conveyance of all materials to site and all labour charges complete for finished item of work excluding Seionarage charges as per Directions of Eng-in- Charge. | 1 Cum |  |  | 117
5 | Plastering with CM(1:5), 20 mm thick for unevenfaces of walls with sponze finish at all heights including cost and conveyance charges of cement and all other materials to site, scaffolding charges, seigniorage charges, incidental and operational charges, all labour charges for mixing mortar, finishing, all leads and lifts, curing, cutting grooves , excluding Seionarage Charges etc., complete for finished item of work and as directed by the Engineer in charge. | 1 Cum |  |  | 130
6 | Supply and erection of MS gate made out of MS rods, angles,channels, flats etc. for main entrance gate fixed in to the gate pillars including cost and conveyance of all the materials, fabrication charges,fixing charges, labour charges etc., complete for finished item of work as directed by the Engineer-in-charge. | 1 Kg | 250 | 250 | 250

## OD SS-Sch IV
Schedule-IV : Supply and Construction of Borewell for new 33/11KV Outdoor Sub-station
Sl. No. | Description of work | Unit | Quantity
1 | Site investigation charges for locating bore well point. | 1 Job | 1 Job
2 | Drilling of 165mm size Bore Well as directed by the Engineer in charge including cost of labour , flushing of borewell, transportation and hire charges for drilling equipment and all taxes complete as per the directions of the Engineer in charge for the finished item of work. | 1RM | 60
3 | Supplying & fixing of PVC heavy duty casing pipe of 180mm dia , 10kg/sqcm for the above Bore hole including cost & conveyance of all materials ,labour ,leads, and lifts and all taxes etc., complete as per the directions of the Engineer in charge for the finished item of work. | 1 RM | 60
4 | Supply, transportation & fixing of Single Phase submersible motor pump set , 21 stage (Crompton / Kirloskar / CRI / L&T / Varsha /Texmo make) of approved type suitable for 165mm dia bore well , as directed by Engineer in charge,of approved quality & make including nipples, bends, couplings etc., including cost & conveyance of all materials, labour charges, fitted with SIEMENS/ CROMPTON make starter with panel board fitted with related fittings such as Ammeter , volt meter and including nuts & bolts and GI sheet bore cover complete as per the directions of the Engineer in charge for the finished item of work.
a | 1.0 HP | Each | 1
b | 1.5 HP | Each | 1
5 | Supplying & fixing 40 mm dia HDPE pipe (12kg/Sqcm) of approved quality & make including nipples, bends, couplings etc., complete for finished item of work from bore well to delivery including cost & conveyance of all materials, specials\l fixtur | 1 RM | 60
6 | Providing and placing on terrace (at all floor levels) 1000 Ltr capasity Polyethylene water storage tank double layer of SYNTEX or approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but without fittings and base support for tanks etc., complete for finished item of work as directed by the Engineer-in-charge. | Each | 1
7 | Supply & fixing of Submersible Flat cable 2.5sq.mm or 3/20 equalint (Finolex) wire including cost & conveyance and all labor charges with all leads ans lifts and all other incidental charges etc; complete. | 1 RM | 135
FOR SITES WHERE BORE WELL DIGGING IS NOT POSSIBLE TAP CONNECTION WITH TAP WATER STORAGE SUMP
1 | Earth work excavation in ordinary soils by manual means upto 3m depth for foundations and depositing on bank for all lifts and with an initial lead of 10m including all operational, incidental, labour charges such as shoring ,sheeting, planking, strutting, etc. complete for finished item of work excluding dewatering charges etc as per SS - 20 B (APSS 308) for water tank of size ( 2.0 MX2.5M X2.3 M ). | 1 Cum | 25
2 | Filling with useful available excavated earth (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum | 25
3 | Filling with sand in foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including, seigniorage cost and conveyance of water to work site and all operational, incidental, labour charges, hire charges of T & P etc., complete for finished item of work. (APSS NO. 309 & 310) | 1 Cum | 1.5
4 | Plain Cement concrete (1:4:8) using 40 mm metal with concrete mixer including seigniorage, cost and conveyance of all materials and all labour charges complete. | 1 Cum | 1.5
5 | Construction of brick masonry in CM 1:6 using well burnt country bricks including seigniorage, cost and conveyance of all materials all labour charges etc., complete. Ground Floor | 1 Cum | 6
6 | Plastering with CM (1:5), 12 mm thick in one coat for inernal faces of walls, ceilings etc.,including seigniorage, cost and conveyance of all materials all labour charges etc, complete. Ground Floor | 1 Sqm | 35
7 | Providing HYSD/TMT/MS Steel bars(Fe415/Fe500 grade as per IS1786-1979) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs,spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc., complete for finished item of work in all floors. | 1 MT | 0.1
8 | RCC M- 25 Desgin mix (380 Kg Cement) for slab corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregate) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and including Seigniorage charges, sales & other taxes on all materials including all operational, incidental and labour charges such as machine mixing, laying concrete, curing and steel centering with wooden scaffolding etc.,complete but excluding cost of steel and its fabrication charges for finished item of work. | 1 Cum | 1
9 | Single Phase 1 HPMono-block Motor including giving Pipe line Connections with all bends, couplings and Running Joints etc., complete. | Each | 1

## DT-160KVA-supply
BoQ for - Supply of 3-Ph DTRs and structure materials |  |  | No of DTs: | 1
Item No. | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Supply of 3 Phase 160 KVA DTRs and structure materials
1 | Supply of 3Ø 160 KVA Amorphous / CRGO core CSP type aluminium wound Distribution Transformers with BEE 5 star losses as per specification | Each | 1 | 1
2 | Supply of 9.1M 280Kg WL PSCC Poles as per Specification and drawing | Each | 2 | 2
3 | Supply of 8.0 Mts long 200KG WL PSCC poles as per Specification and drawing | Each | 2 | 2
4 | Supply of 11 KV 200 Amps Tilting type AB switch complete with polymer insulators as per Technical specifications | Each | 1 | 1
5 | Supply of 11 KV HG Fuse sets with Polymer Insulators as per Technical specifications | Each | 1 | 1
6 | Supply of 11 KV Top Cleat with MS Back Clamp 50x6 mm MS Flat for 9.1 Mts PSCC Pole as per specification and drawing | Each | 1 | 1
7 | Supply of Stay Clamps for 9.1Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 2 | 2
8 | Supply of Stay Clamps for 8Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 2 | 2
9 | Supply of 11KV Polymer insulators with pins as per specification. | Each | 4 | 4
10 | Supply of 11KV Polymer Disc Insulators (B&S) with metal parts (B&S) suitable for 100 Sqmm AAAC as per specification. | Each | 3 | 3
11 | Supply of LT 3-ph 5 W Cross arm with 50x6 mm MS Back clamps for 9.1 Mts PSCC pole as per drawing and specification | Each | 2 | 2
12 | Supply of LT Shackle Insulators with metal parts as per Technical specification | Each | 10 | 10
13 | Supply of M.S. Channel 75X40 mm as per Technical Specification | Kgs | 29.444 | 29.444
14 | Supply of M.S. Angle 50X50X6 mm as per Technical Specification | Kgs | 9.54 | 9.54
15 | Supply of M.S. Flat 50X6 mm as per Technical Specification | Kgs | 11.592 | 11.592
16 | LT Distribution box & Terminal arrangements
16.1 | Supply of A Type Distribution Box with 300A, 500V Knife type Fuse Units for 2-Feeders (SMC) for 3-Ph DTRs as per specification | Each | 1 | 1
16.2 | Supply of Single core 185 Sq.mm XLPE cable as per Technical specification | Mts | 60 | 60
17 | Earthing
17.1 | Supply of CI earth pipe of 50 mm dia., 2.0 Mt. Long as per specification | Each | 1 | 1
17.2 | Supply of GI earth pipe of 40 mm dia., 1.8 Mt. Long as per specification | Each | 2 | 2
17.3 | Supply of GI earth flat 25x3 mm size as per specification | Kgs | 25 | 25
17.4 | Supply of GI wire No.8 as per Specification | Kgs | 2 | 2
18 | Supply of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) as per drawing & Technical Specification | Each | 1 | 1
19 | Supply of Danger Notice Board of size 250x200mm for high voltage system as per drawing & Technical Specification | Each | 1 | 1

## DT-160KVA-erection
Erection of DTRs |  |  | No fo DTRs: | 1
Item No. | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Erection of 3 Phase 160 KVA DTRs and structure materials
1 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
1.1 | For 8m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 2
1.2 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 2
2 | Erection of PSCC Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
2.1 | 8m/200 KG PSCC Pole | Each |  | 2
2.2 | 9.1m/280 KG PSCC Pole | Each |  | 2
3 | Concreting of the pole locations of pit size 0.6x0.6x1.5Mts. with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. (For 9.1 Mts PSCC Poles) | Each |  | 2
4 | Erection and commissioning of 3Ø 160 KVA Distribution Transformer on the plinth carefully without causing any damage to bushing including labour and transport to site from stores complete including earthing as per department standards and Geotagging -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification and drawing | Each | 1 | 1
5 | Erection of 11 KV AB switch complete with polymer insulators with operating pipe with earthing arrangement and necessary jumpers with fixing of necessary mounting arrangements, supporting M.S channel with back clamp for fixing of Insulators,double earthing incl supply of Bolts, Nuts & Washers, cost of Jumpers as per Technical specification and drawing which includes fabrication charges,painitng and consumables but excluding the cost of M.S. Materials | Each | 1 | 1
6 | Erection of 11 KV HG Fuse sets complete with double earthing as per specification and drawing | Each | 1 | 1
7 | Erection of 11 KV Cross arm with back clamp suitbale for tapping HT Line (Inline/Dead end) incl supply of Bolts, Nuts & Washers and fabrication charges,painitng and consumables but excluding the cost of M.S. Materials as per the direction of Engineer - Incharge | Each | 1 | 1
8 | Erection of 11KV Top cleat with clamp incl supply of Bolts, Nuts & Washers as per Specification and drawing | Each | 1 | 1
9 | Fixing of 11 KV Polymer Insulators with pin binding | Each |  | 4
10 | Fixing of 11 KV Polymer Disc Insulators with metal parts | Each |  | 3
11 | Construction of DTR plinths
11.1 | DTR PLINTH WITH 5' X 5' X 6" SLAB AND 9" COLUMNS : Construction of pillar mounted Distribution transformer plinth using RCC M 20 grade (1:1.5:3 ) with 5'x5'x6" slab with column 6' above ground level. - : Excavation of pit of size 4’x4’x6' 6", laying bed concrete with CC(1:4:8) using 40mm HBG metal for 6” depth, footing of size (4’x4’x1' 6" ),column size 9”x9”x4'6”(below ground), 9"x9"x6' (above ground), cross beams in plus shape 4'x9”x12”, slab size 5’x5’x6”, providing reinforced steel 10mm rod both sides for footings and slab at 6" spacing, 4 nos 12mm rod for columns and beams with 8mm stirrups @ 6" centre to centre, re-filling the hollow portion with excavated earth, plastering CM (1:5) 12mm thick and painting one coat to slabs, column and beam..(for erection of 63KVA and above capacities) including seigniorage charges as per Technical specification including all materials and labour and as per directions of Eng-in-Charge. | Each | 1 | 1
or (As per requirement)
11.2 | DTR PLINTH WITH BRICK MASONARY WALL OF THICKNESS 9" : Construction of DTR plinths- Size 4'x4'x6'(above ground) and 4'x4'x3' (below ground) with Brick masonry wall- Excavation of pit of size 4’x4’x3’, laying bed concrete with CC(1:4:8) using 40mm HBG metal for 6” depth,Construction of distribution transformer plinth with 9" thick 8'6" height Brick masonry wall in CM (1:6) allround, filling the hollow portion with sand, andlaying PCC (1:2:4 ) with 12 to 20 mm HBg metal of 4" thick plastering all-round the outer side of wall with CM (1:5) 20 mm thick and white washing two coats including seigniorage charges as per Technical specification including all materials and labour and as per directions of Eng-in-Charge. | Each | 1 | 1
12 | LT Distribution box & Terminal arrangements
12.1 | Erection of A Type Distribution Box with 300A, 500V Knife type Fuse Units for 2-Feeders for 3-Ph DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables as per as per specification and drawing. | Each | 1 | 1
12.2 | Erection of LT terminal arrangements with Single core 185 Sq.mm LT XLPE Cable from LT bushing of DTR to LT Distribution box and from LT Distribution box to OH line (Double Circuit) including transport, supply & fixing of plastic cleats at equal intervals mounted on 4nos angle cross arms of 25x25x3mm size for running LT XLPE (Double Circuit) cable neatly as per departmental standards so that cable load is not incident either on OH line or on Distribution box. Aluminium lugs of suitable size are to be supplied for each phase of distribution box at Incoming and out going terminals and crimped properly using crimping tool and incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables as per departmental standards as per Technical specification | Each Loc | 1 | 1
13 | Fixing of LT 3-Ph 5 wire cross arms with back clmaps, supply of nuts & bolts as per specification | Each | 1 | 2
14 | Fixing of LT Shackle Insulators with metal parts including binding wherever necessary as per specification. | Each |  | 10
15 | Earthing with 25x3mm GI flat duly earthing of DTR Structure equipment, and DTR as per Specification including erection of 1No CI pipe 50 mm dia., 2.0 Mt. Long and 2nos GI pipes, 40 mm dia., 1.8 Mt. Long including supply of bentonite powder and mixing soil with ratio 1:6 and giving connections etc., as per departmentat standards. for 3Ph DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables & supply of 3 Nos Earth Pit Collars (2Ft x 2 Ft) as per specification | Each Loc | 1 | 1
16 | Fixing of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) at DTR loacations as per the drawing including transport asper specification | Each | 1 | 1
17 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 1 | 1

## DT-25KVA-supply
BoQ for - Supply of 3-Ph DTRs and structure materials |  |  | No of DTs: | 1
Item No. | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Supply of 3 Phase 25 KVA DTRs and structure materials
1 | Supply of 3Ø 25 KVA Amorphous / CRGO core CSP type aluminium wound Distribution Transformers with BEE 5 star losses as per specification | Each | 1 | 1
2 | Supply of 9.1M 280Kg WL PSCC Poles as per Specification and drawing | Each | 2 | 2
3 | Supply of 8.0 Mts long 200KG WL PSCC poles as per Specification and drawing | Each | 2 | 2
4 | Supply of 11 KV 200 Amps Tilting type AB switch complete with polymer insulators as per Technical specifications | Each | 1 | 1
5 | Supply of 11 KV HG Fuse sets with Polymer Insulators as per Technical specifications | Each | 1 | 1
6 | Supply of 11 KV Top Cleat with MS Back Clamp 50x6 mm MS Flat for 9.1 Mts PSCC Pole as per specification and drawing | Each | 1 | 1
7 | Supply of Stay Clamps for 9.1Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 2 | 2
8 | Supply of Stay Clamps for 8Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 2 | 2
9 | Supply of 11KV Polymer insulators with pins as per specification. | Each | 4 | 4
10 | Supply of 11KV Polymer Disc Insulators (B&S) with metal parts (B&S) suitable for 100 Sqmm AAAC as per specification. | Each | 3 | 3
11 | Supply of LT 3-ph 5 W Cross arm with 50x6 mm MS Back clamps for 9.1 Mts PSCC pole as per drawing and specification | Each | 1 | 1
12 | Supply of LT Shackle Insulators with metal parts as per Technical specification | Each | 5 | 5
13 | Supply of M.S. Channel 75X40 mm as per Technical Specification | Kgs | 56.644 | 56.644
14 | Supply of M.S. Angle 50X50X6 mm as per Technical Specification | Kgs | 25.875 | 25.875
15 | Supply of M.S. Flat 50X6 mm as per Technical Specification | Kgs | 13.992 | 13.992
16 | LT Distribution box & Terminal arrangements
16.1 | Supply of Distribution Box with 100A, 500V Knife type Fuse Units for 1-Feeder (SMC) for 3-Ph DTRs as per specification | Each | 1 | 1
16.2 | Supply of Single core 50 Sq.mm XLPE cable as per Technical specification | Mts | 45 | 45
17 | Earthing
17.1 | Supply of CI earth pipe of 50 mm dia., 2.0 Mt. Long as per specification | Each | 1 | 1
17.2 | Supply of GI earth pipe of 40 mm dia., 1.8 Mt. Long as per specification | Each | 2 | 2
17.3 | Supply of GI earth flat 25x3 mm size as per specification | Kgs | 25 | 25
17.4 | Supply of GI wire No.8 as per Specification | Kgs | 2 | 2
18 | Supply of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) as per drawing & Technical Specification | Each | 1 | 1
19 | Supply of Danger Notice Board of size 250x200mm for high voltage system as per drawing & Technical Specification | Each | 1 | 1

## DT-25KVA-erection
Erection of DTRs |  |  | No fo DTRs: | 1
Item No. | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Erection of 3 Phase 25 KVA DTRs and structure materials
1 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
1.1 | For 8m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 2
1.2 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 2
2 | Erection of PSCC Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
2.1 | 8m/200 KG PSCC Pole | Each |  | 2
2.2 | 9.1m/280 KG PSCC Pole | Each |  | 2
3 | Concreting of the pole locations of pit size 0.6x0.6x1.5Mts. with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. (For 9.1 Mts PSCC Poles) | Each |  | 2
4 | Erection and commissioning of 3Ø 25 KVA Distribution Transformer on structure carefully without causing any damage to bushing including labour and transport to site from stores complete including earthing as per department standards and Geotagging -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification and drawing | Each | 1 | 1
5 | Erection of 11 KV AB switch complete with polymer insulators with operating pipe with earthing arrangement and necessary jumpers with fixing of necessary mounting arrangements, supporting M.S channel with back clamp for fixing of Insulators,double earthing incl supply of Bolts, Nuts & Washers, cost of Jumpers as per Technical specification and drawing which includes fabrication charges,painitng and consumables but excluding the cost of M.S. Materials | Each | 1 | 1
6 | Erection of 11 KV HG Fuse sets complete with double earthing as per specification and drawing | Each | 1 | 1
7 | Erection of 11 KV Cross arm with back clamp suitbale for tapping HT Line (Inline/Dead end) incl supply of Bolts, Nuts & Washers and fabrication charges,painitng and consumables but excluding the cost of M.S. Materials as per the direction of Engineer - Incharge | Each | 1 | 1
8 | Erection of 11KV Top cleat with clamp incl supply of Bolts, Nuts & Washers as per Specification and drawing | Each | 1 | 1
9 | Fixing of 11 KV Polymer Insulators with pin binding | Each |  | 4
10 | Fixing of 11 KV Polymer Disc Insulators with metal parts | Each |  | 3
11 | Erection of SP Structure (seating arrangement) complete for mounting 3-Ph 25KVA Transformer including earthing as per departmental standards with 75x40mm MS Channels, 50x50x6mm MS Angles and 50x6mm MS flat as per specification which includes supply of M.S. Bolts , Nuts and Washers, fabrication charges,painitng and consumables but excluding the cost of M.S. Materials | Each | 1 | 1
12 | LT Distribution box & Terminal arrangements
12.1 | Erection of Distribution Box with 100A, 500V Knife type Fuse Units for 1-Feeder (SMC) for 3-Ph DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables as per as per specification and drawing. | Each | 1 | 1
12.2 | Erection of LT terminal arrangements with Single core 50 Sq.mm LT XLPE Cable from LT bushing of DTR to LT Distribution box and from LT Distribution box to OH line through the DTR LV CT Meter including including transport, supply & fixing of plastic cleats at equal intervals mounted on 4nos angle cross arms of 25x25x3mm size for running LT XLPE cable neatly as per departmental standards so that cable load is not incident either on OH line or on fuse box. Aluminium lugs of suitable size are to be supplied for each phase of distribution box at Incoming and out going terminals and crimped properly using crimping tool as per departmental standards as per Technical specification | Each Loc | 1 | 1
13 | Fixing of LT 3-Ph 5 wire cross arms with back clmaps, supply of nuts & bolts as per specification | Each | 1 | 1
14 | Fixing of LT Schackle Insulators with metal parts including binding wherever necessary as per specification. | Each |  | 5
15 | Earthing with 25x3mm GI flat duly earthing of DTR Structure equipment, and DTR as per Specification including erection of 1No CI pipe 50 mm dia., 2.0 Mt. Long and 2nos GI pipes, 40 mm dia., 1.8 Mt. Long including supply of bentonite powder and mixing soil with ratio 1:6 and giving connections etc., as per departmentat standards. for 3Ph DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables & supply of 3 Nos Earth Pit Collars (2Ft x 2 Ft) as per specification | Each Loc | 1 | 1
16 | Fixing of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) at DTR loacations as per the drawing including transport asper specification | Each | 1 | 1
17 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 1 | 1

## DT-16KVA-supply
BoQ for - Supply of 1-Ph DTRs and structure materials |  |  | No of DTs: | 1
Item No. | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Supply of 1 Phase 16 KVA DTRs and structure materials
1 | Supply of 1Ø 16 KVA Amorphous / CRGO core CSP type aluminium wound Distribution Transformers with BEE 5 star losses as per specification | Each | 1 | 1
2 | Supply of 9.1M 280Kg WL PSCC Poles as per Specification and drawing | Each | 1 | 1
3 | Supply of 8.0 Mts long 200KG WL PSCC poles as per Specification and drawing | Each | 1 | 1
4 | Supply of 6.3KV/S-Ph TT AB switch complete with Polymer Insulators, operating pipe as per specification | Each | 1 | 1
5 | Supply of 6.3 KV HG fuse set with Polymer Insulators as per specification | Each | 1 | 1
6 | Supply of 11 KV Top Cleat with MS Back Clamp 50x6 mm MS Flat for 9.1 Mts PSCC Pole as per specification and drawing | Each | 1 | 1
7 | Supply of Stay Clamps for 9.1Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 2 | 2
8 | Supply of Stay Clamps for 8Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 1 | 1
9 | Supply of 11KV Polymer insulators with pins as per specification. | Each | 1 | 1
10 | Supply of 11KV Polymer Disc Insulators (B&S) with metal parts (B&S) suitable for 100 Sqmm AAAC as per specification. | Each | 1 | 1
12 | Supply of LT Shackle Insulators with metal parts as per Technical specification | Each | 2 | 2
13 | Supply of M.S. Channel 75X40 mm as per Technical Specification | Kgs | 15.776 | 15.776
14 | Supply of M.S. Angle 50X50X6 mm as per Technical Specification | Kgs | 10.215 | 10.215
15 | Supply of M.S. Flat 50X6 mm as per Technical Specification | Kgs | 8.85 | 8.85
16 | LT Distribution box & Terminal arrangements
16.1 | Supply of Distribution Box with 100A, 500V Knife type Fuse Units for 1-Feeder (SMC) for S-Ph DTRs as per specification | Each | 1 | 1
16.2 | Supply of Single core 50 Sq.mm XLPE cable as per Technical specification | Mts | 20 | 20
17 | Earthing
17.2 | Supply of GI earth pipe of 40 mm dia., 1.8 Mt. Long as per specification | Each | 2 | 2
17.3 | Supply of GI earth flat 25x3 mm size as per specification | Kgs | 20 | 20
17.4 | Supply of GI wire No.8 as per Specification | Kgs | 2 | 2
18 | Supply of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) as per drawing & Technical Specification | Each | 1 | 1
19 | Supply of Danger Notice Board of size 250x200mm for high voltage system as per drawing & Technical Specification | Each | 1 | 1

## DT-16KVA-erection
Erection of 1-Ph DTRs |  |  | No fo DTRs: | 1
Item No. | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Qty per DTR | Total Qty
Erection of 1 Phase 16 KVA DTRs and structure materials
1 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
1.1 | For 8m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 1
1.2 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit |  | 1
2 | Erection of PSCC Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
2.1 | 8m/200 KG PSCC Pole | Each |  | 1
2.2 | 9.1m/280 KG PSCC Pole | Each |  | 1
3 | Concreting of the pole locations of pit size 0.6x0.6x1.5Mts. with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. (For 9.1 Mts PSCC Poles) | Each |  | 1
4 | Erection and commissioning of 1Ø 16 KVA Distribution Transformer on structure carefully without causing any damage to bushing including labour and transport to site from stores complete including earthing as per department standards and Geotagging -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification and drawing | Each | 1 | 1
5 | Erection of 6.3 KV S-Ph AB switch complete with polymer insulators with operating pipe with earthing arrangement and necessary jumpers with fixing of necessary mounting arrangements, supporting M.S channel with back clamp for fixing of Insulators,double earthing incl supply of Bolts, Nuts & Washers, cost of Jumpers as per Technical specification and drawing which includes fabrication charges,painitng and consumables but excluding the cost of M.S. Materials | Each | 1 | 1
6 | Erection of 6.3 KV HG Fuse sets complete with double earthing as per specification and drawing | Each | 1 | 1
7 | Erection of Stay clamp set for fixing of 11 KV Polymer Disc Insulators | Each | 1 | 1
8 | Erection of 11KV Top cleat with clamp incl supply of Bolts, Nuts & Washers as per Specification and drawing | Each | 1 | 1
9 | Fixing of 11 KV Polymer Insulators with pin binding | Each |  | 1
10 | Fixing of 11 KV Polymer Disc Insulators with metal parts | Each |  | 1
10 | Erection of SP Structure (seating arrangement) complete for mounting 1-Ph 16KVA Transformer including earthing as per departmental standards with 75x40mm MS Channels, 50x50x6mm MS Angles and 50x6mm MS flat as per specification which includes supply of M.S. Bolts , Nuts and Washers, fabrication charges,painitng and consumables but excluding the cost of M.S. Materials | Each | 1 | 1
11 | LT Distribution box & Terminal arrangements
11.1 | Erection of Distribution box with 100A, 500V Knife type Fuse Units for 1-Feeder (SMC) for 1-Ph DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables as per as per specification and drawing. | Each | 1 | 1
11.2 | Erection of LT terminal arrangements with Single core 50 Sq.mm LT XLPE Cable from LT bushing of DTR to LT Distribution box and from LT Distribution box to OH line through the DTR LV CT Meter including including transport, supply & fixing of plastic cleats at equal intervals mounted on 4nos angle cross arms of 25x25x3mm size for running LT XLPE cable neatly as per departmental standards so that cable load is not incident either on OH line or on fuse box. Aluminium lugs of suitable size are to be supplied for each phase of distribution box at Incoming and out going terminals and crimped properly using crimping tool as per departmental standards as per Technical specification | Each Loc | 1 | 1
12 | Fixing of LT Side arm with Struts with back clamps and strut clamps suitable for LT Take off arrangement,with 50x50x6mm MS Angles and 50x6mm MS flat as per specification which includes supply of M.S. Bolts , Nuts and Washers, fabrication charges,painitng and consumables but excluding the cost of M.S. Materials as per specification and drawing. | Each |  | 1
13 | Fixing of LT Shackle Insulators with metal parts including binding wherever necessary as per specification. | Each |  | 2
14 | Earthing with 25x3mm GI flat duly earthing of DTR Structure equipment, and DTR as per Specification including erection of 2nos GI pipes, 40 mm dia., 1.8 Mt. Long including supply of bentonite powder and mixing soil with ratio 1:6 and giving connections etc., as per departmentat standards. for SPh DTRs incl supply of Bolts, Nuts & Washers and cost of fabrication charges for labour and consumables & supply of 2 Nos Earth Pit Collars (2Ft x 2 Ft) as per specification | Each Loc | 1 | 1
15 | Fixing of sign board of weather proof plate of size 1 feet x 1 feet made of CR sheet 14 guage (1.6mm) at DTR loacations as per the drawing including transport asper specification | Each | 1 | 1
16 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 1 | 1

## LT 9.1-55Sqmm supply
|  |  |  | No fo KM | 10
Schedule: LT lines Supply
Item No. | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | CD Qty | Appx Qty required for KM | Total Qty
Supply of LT 3-Ph 5Wire line with 55 Sqmm AAA Conductor over 9.1Mts PSCC Poles
1 | Supply of 9.1 Mts 280Kg PSCC poles as per Technical specification | Each | 25 | 25 | 250
2 | Supply of 8 Mts 200Kg PSCC poles (for struts) as per Technical specification | Each | 2 | 4 | 40
3 | Supply of 55Sqmm AAAC as per Technical specification | Km | 5.1 | 5.1 | 51
4 | Supply of MS Stay Set with LT Guy Insulator and 7/2.50mm GI stay wire Complete with clamps as per Drawing & Technical specification | Each | 4 | 2 | 20
5 | Supply of Stay Clamps for 9.1Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 4 | 6 | 60
6 | Supply of Stay Clamps for 8Mts PSCC Pole with 50X6mm MS Flat Including Bolts & Nuts | Set | 4 | 4 | 40
7 | Supply of LT 3-Ph 5 wire cross arm with back clamps as per specification & drawing | Each | 25 | 27 | 270
8 | Supply of LT 3-Ph 5 wire side arm with 75X40 mm MS Channel length 1.80 Mtrs,50X50X6mm MSAngle length 1.6 Mtrs, Back Clamps and Stay clamps as per Technical specification & drawing | Each | 0 | 2 | 20
9 | Supply of 2 Nos LT 3-Ph 5 wire side arms with 75X40 mm MS Channal length 1.80 Mtrs with fish plates and 2Nos 50X50X6mm MS Angles of length 1.6 Mtrs as struts and Stay clamps for dead end poles as per Technical specification & drawing | Each | 0 | 1 | 10
10 | Supply of LT Pin Insulators with Pins as per Technical specification | Each | 52 | 68 | 680
11 | Supply of LT Shakle Insulators with metal parts as per Technical specification | Each | 48 | 60 | 600
12 | Supply of C.I.Knobs as per specification | Each | 25 | 17 | 170
13 | Supply of Foot Cross arm with 50X50X6 mm MS angle of 0.61Mts.(2feet) long with Back Clamps as per Technical specification & drawing | Each | 0 | 25 | 250

## LT-9.1-55Sqmm erection
Schedule: LT lines Erection |  |  | No fo KM | 10
Item No. | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Appx Qty required for KM | Total Qty
Erection of LT 3-Ph 5Wire line with 55 Sqmm AAA Conductor over 9.1Mts PSCC Poles
1 | Detailed Survey, pit marking and way leaves Clearence including Clearing of heavy jungle, Cutting and removing other kind of tree | KM | 1 | 10
2 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
2.1 | For 8m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 2 | 20
2.2 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 12 | 120
3 | Excavation of pole pit in hard rock by drilling where blasting is not possible |  | -
3.2 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 1 | 10
4 | Excavation of pole pit in all soils with pole digging Machine | Pit | 14 | 140
5 | Excavation of Stay pit size 0.45 x 0.45 x 1.34 Mts. In all soils except hard murrum and disintegrated rock which requires blasting | Pit | 2 | 20
6 | Erection of 9.1Mts PSCCPoles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole up to pit location wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification | Each | 25 | 250
7 | Erection of 8Mt./200Kg WL PSCC pole as Struts whereever necessary in the existing line including fixing of required clamps, including loading, unloading and transport where ever necessary and back filling the pits after erection of pole with excavated earth /extra earth and levelling the site without any lead as per specification. | Each | 4 | 40
8 | Erection of MS Stay Set with LT Guy Insulator and 7/2.50mm GI stay wire Complete as per Drawing where ever necessary including Erection of anchor rod and anchor plate in the pit, clamps fixing supply of nuts & bolts and connecting the stay to the pole as per specification | Each | 2 | 20
9 | Concreting of the pole locations of pit size 0.6x0.6x1.5Mts. up to 0.1Mts. as base concrete before erecting the pole and 1.4Mts. upto ground level after erecting the pole as pole cocrete with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary as per specification. | Each | 7 | 70
10 | Concreting of Stay locations wherever necessary for anchor rod of the stay set up to ground level of size 0.45x0.45x1.34Mts. with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification wherever necessary. | Each | 2 | 20
11 | Paving out and stringing the 55Sqmm AAAC over existing supports / newly erected supports and transport to the location and handling charges including pin binding, jointing, clamping, jumpering and strain insulator binding etc duly maintaining standard ground clearances duly following the technical specification | Conductor KM | 5 | 50
12 | Fixing of LT 3-Ph 5 wire cross arms with back clmaps, supply of nuts & bolts as per specification | Each | 27 | 270
13 | Fixing of LT 3-Ph 5 wire side arm with sturt with clamps, supply of nuts & bolts as per specification | Each | 2 | 20
14 | Fixing of 2 Nos LT 3-Ph 5 wire side arms with 75X40 mm MS Channal length 1.80 Mtrs with fish plates and 2Nos 50X50X6mm MS Angles of length 1.6 Mtrs as struts and Stay clamps for dead end poles, supply of nuts & bolts including transport, as per specification & drawing | Each | 1 | 10
15 | Fixing of Foot Cross arm with 50X50X6 mm MS angle of 0.61Mts.(2feet) long with Back Clamp for all the poles before erection, including transport,supply of nuts & bolts, as per specification | Each | 25 | 250
16 | Fixing of LT Pin Insulators with Pins including pin binding wherever necessary asper specification | Each | 68 | 680
17 | Fixing of LT CI Knob including pin binding wherever necessary asper specification | Each | 17 | 170
18 | Fixing of LT Shakle Insulators with metal parts including binding wherever necessary as per specification. | Each | 60 | 600
19 | Numbering of poles with AC Black paint back ground and numbering with white paint including cost of all materials . | Each | 25 | 250

## 11KV-9.1 M-supply
BOQ Supply of Materials for 11 KV Line on 9.1 mtrs PSCC Poles with 100Sq.mm AAA conductor-For 10 KM
|  |  | Total CKM |  | 10
Line Item No. | 9.1 mtrs PSCC Poles with 100 Sq.mm | Cost Data Qty | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Quantity for 10 KM | Unit Ex-works price | Total Ex-works Amount | Contractor Profit (Amount) @ 13.615% | Total Amount incl. Contractor Profit | Workers Welfare Cess payable (Amount) @ 1% | GST payable on the price quoted if Contract is awarded (Amount) @18% | Total Amount per line item | SSR Reference
1 |  |  | 2 | 3 | 4 | 5 | 6 = 4x5
1 | 21 | 22 | Supply of 9.1M 280Kg WL PSCC Poles as per Specification and drawing | Each | 210 | 4577.1186 | 961194.9153 | 130866.6877 | 1092061.603 | 10920.616 | 196571.0885 | 1299553.3075 | Cost Data 2022-23, Sl.No.5 of Section 1(b)-Poles, Pg 4
2 | 4 | 4 | Supply of 8.0 Mts long 200KG WL PSCC poles as per Specification and drawing | Each | 40 | 3216.1017 | 128644.0678 | 17514.8898 | 146158.9576 | 1461.5896 | 26308.6124 | 173929.1596 | Cost Data 2022-23 SL.no.7 of Section 1(b)-Poles, Pg 4
3 | 18 | 20 | Supply of 1.07 Mtrs. V 'X' arms With Back Clamp made up of 75X40 mm MS Channel and 50X6 mm MS Flat as per specification and drawing for 9.1 Mtrs PSCC Pole | Set | 180 | 1274.5961 | 216681.3373 | 29501.1641 | 246182.5014 | 2461.825 | 44312.8502 | 292957.1766 | Data 2A
4 | 18 | 20 | Supply of 11 KV Top Cleat with MS Back Clamp 50x6 mm MS Flat for 9.1 Mts PSCC Pole as per specification and drawing | Each | 180 | 496.9576 | 84482.7966 | 11502.3328 | 95985.1294 | 959.8513 | 17277.3233 | 114222.3039 | Data 12
5 | 1 | 3 | Supply of 1.5 Mtrs 11KV Tapping cross Arm made up of 100X50 mm MS Channel and Back Clamp made up of 75X8 mm MS Flat for 9.1 Mts PSCC Pole as per specification and drawing | Each | 10 | 1172.0537 | 42153.1373 | 5739.1496 | 47892.2869 | 478.9229 | 8620.6116 | 56991.8214 | Data 2
6 | 65 |  | Supply of M.S. Channel 75X40 mm as per Technical Specification | Kgs | 650
7 | 36 |  | Supply of M.S. Angle 50X50X6 mm as per Technical Specification | Kgs | 360
8 | 26 |  | Supply of M.S. Flat 50X6 mm as per Technical Specification | Kgs | 260
9 | 2 | 4 | Supply of Stay set with Clamps complete including bow,binding of eye bolts, anchor rods, guy insulators and GI Stay wire 7/3.15 mm (with base plate) as per specification | Each | 20
10 | 4 | 4 | Supply of Stay Clamps for 9.1Mts PSCC Pole with 75X8mm MS Flat Including Bolts & Nuts for strut poles | Set | 40 | 148.2203 | 10226.1071 | 1392.2845 | 11618.3916 | 116.1839 | 2091.3105 | 13825.886 | Weight of Stay Clamp is 1.83 Kg for 8 Mtrs PSCC Pole-Cost Data 3f.7
11 | 4 | 4 | Supply of Stay Clamps for 8Mts PSCC Pole with 75X8mm MS Flat Including Bolts & Nuts for strut poles | Set | 40
12 | 57 | 60 | Supply of 11KV Polymer insulators with pins as per specification. | Each | 570 | 354.2373 | 244423.7288 | 33278.2907 | 277702.0195 | 2777.0202 | 49986.3635 | 330465.4032 | Cost data 2022-23, Sl No 3 of Section 2(b)-11KV Insulators, Pg 6
13 | 12 | 12 | Supply of 11KV Polymer Disc Insulators (B&S) with metal parts (B&S) suitable for 100 Sqmm AAAC as per specification. | Each | 120 | 361.1915 | 54178.7288 | 7376.4339 | 61555.1627 | 615.5516 | 11079.9293 | 73250.6437 | Cost Data 2022-23, Sl.No 7 & 8 of Section 2(b)-11KV Insulators, Pg 6
14 | 21 |  | Supply of Spiral earth coil as per Specification | Each | 210 | 254.4915 | 55988.1356 | 7622.7847 | 63610.9203 | 636.1092 | 11449.9656 | 75696.9951 | Data 29
15 | 3.06 | 3.06 | Supply of 100Sq.mm AAA Conductor | KM | 30.6 | 95315.9322 | 2916667.5254 | 397104.2836 | 3313771.809 | 33137.7181 | 596478.9256 | 3943388.4527 | Cost Data 2022-23, Sl.No 5 of Section 4, Pg 9
16 | 8.4 |  | Supply of Aluminium T Clamps for 100sq.mm AAA conductor (6 Nos T Clamps shall be used for each cutpoint, for double jumpering work for cutpoints) | Each | 84
17 | 4.8 |  | Supply Pad Clamps suitable for AB Switch (12 Nos Pad Clamps shall be provided at each AB Switch for double jumpering) | Each | 48
18 | 0.4 |  | Supply of 11 KV Isolators (400 A) double break with Post type Insulator as per specifications and drawing. | Each | 4
19 | 0.4 |  | Supply of 40 mm, 1.8Mts GI Earth Pipe as per Specification and drawing. | Each | 4
20 | 4 |  | Supply of GI wire No.8 as per Specification | Kgs | 40
21 | 21 |  | Supply of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp | Each | 210
22 | 1 |  | Supply of Danger Board 250x200mm for high voltage system, the plate shall be made from mild steel sheet of at least 1.6mm thick and vitreous enameled white, with letters, figures and the conventional skull and cross-bones in signal red colour (refer IS:5-1978) on the front side. The rear side of the plate shall also be enamelled and also the corners of the plate shall be rounded off as per the specification IS:2551-1982 | Each | 10 | 121 | 2541 | 345.9572 | 2886.9572 | 28.8696 | 519.6523 | 3435.479 | As per Cost Data 2022-23 Item Sub Head 11 Item 20
23 | 1 | - | Supply of LT 3-ph 5 W Cross arm with 50x6 mm MS Back clamps for 9.1 Mts PSCC pole as per drawing and specification | Each | 10
24 | 4 | - | Supply of LT Pin Insulators with GI Pins as per specification | Each | 40
25 | 5 | - | Supply of Guarding with suitable GI wire, along with necessary supporting channels , Bolts & Nuts as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules . | RMT | 50
|  |  | Total Supply |  |  |  | 4717181.48 | 642244.2585 | 5359425.7385 | 53594.2574 | 964696.6329 | 6377716.6288
Note : If specifications & drawings are not provided in the Bid document for any BoQ items,, relavant REC specifications & Drawings shall be followed.
2. For Iron materials only Net weight of the finished products will be considered billing purpose. Bidders are requested to quote the prices of raw materials accordingly.

## 11KV-9.1M-erection
BOQ- ERECTION of 11 KV Line on 9.1 mtrs PSCC Poles with 100Sq.mm AAA conductor -For 10 Km
|  | Total CKM |  | 10
Line Item No. | Per kM Qty | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Quantity | Unit price | Total Amount (Excluding Taxes) | Contractor Profit (Amount) @ 13.615% | Total Amount incl. Contractor Profit | Workers Welfare Cess payable (Amount) @ 1% | GST payable on the price quoted if Contract is awarded (Amount) @ 18% | Total Amount per line item | Reference
1 |  | 2 | 3 | 4 | 5 | 6 = 4x5
1 | 1 | Detailed GIS Survey, pit marking and way leaves Clearence including Clearing of heavy jungle, Cutting and removing other kind of trees | KM | 10 | 3883 | 38830 | 5286.7045 | 44116.7045 | 441.167 | 7941.0068 | 52498.8784 | Data-1
2 | 0 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
2.1 | 4 | For 8m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 40 | 426.8 | 17072 | 2324.3528 | 19396.3528 | 193.9635 | 3491.3435 | 23081.6598 | Data-2
2.2 | 16 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 160 | 530.2 | 84832 | 11549.8768 | 96381.8768 | 963.8188 | 17348.7378 | 114694.4334 | Data-3
3 | 0 | Excavation of pole pit in hard rock by drilling where blasting is not possible
3.1 | 1 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 10
4 | 4 | Excavation of pole pit in all soils with pole digging Machine | Pit | 40
5 | 2 | Excavation of Stay pit size 0.45 x 0.45 x 1.34 Mts. In all soils except hard murrum and disintegrated rock which requires blasting | Pit | 20 | 194.7 | 3894 | 530.1681 | 4424.1681 | 44.2417 | 796.3503 | 5264.76 | Data-9
6 | 0 | Erection of PSCC Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
6.1 | 4 | 8m/200 KG PSCC Pole | Each | 40 | 4396.997 | 175879.88 | 23946.0457 | 199825.9257 | 1998.2593 | 35968.6666 | 237792.8515 | Data-12
6.2 | 21 | 9.1m/280 KG PSCC Pole | Each | 210 | 7685.425 | 1613939.25 | 219737.8289 | 1833677.0789 | 18336.7708 | 330061.8742 | 2182075.7239 | Data-15
7 | 2 | Erection of MS Stay Set with HT Guy Insulator and 7/3.15mm GI stay wire Complete as per Drawing where ever necessary including Erection of anchor rod and anchor plate in the pit, and connecting the stay to the pole as per departmental standards but excluding excavation of Stay pit of size 0.45x0.45x1.34Mts incl supply of Bolts, Nuts & Washers. | Each | 20 | 363.6362 | 7272.7248 | 990.1815 | 8262.9063 | 82.6291 | 1487.3231 | 9832.8585 | Data-16
8 | 5 | Concreting of the pole locations of pit size 0.6x0.6x1.5Mts. with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. (For 9.1 Mts PSCC Poles) | Each | 50 | 6946.0417 | 347302.0833 | 47285.1786 | 394587.262 | 3945.8726 | 71025.7072 | 469558.8418 | Data-17
9 | 2 | Concreting of 11KV Stay locations wherever necessary for anchor rod of the stay set up to ground level of size 0.45x0.45x1.34Mts. with 1:3:6 cement concreting mix using 20 mm and 12mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. | Each | 20 | 1936 | 38720 | 5271.728 | 43991.728 | 439.9173 | 7918.511 | 52350.1563 | Data-19
10 | 18 | Erection of 1.07 Mtrs. V 'X' arms for PSCC Poles with 75x40 mm MS Channel and Back Clamp with 50X6 mm MS Flat incl supply of Bolts ( 5/8" X 3 "), Nuts & Washers as per Specification and drawing | Each | 180 | 163.3588 | 29404.584 | 4003.4341 | 33408.0181 | 334.0802 | 6013.4433 | 39755.5416 | Data-20
11 | 18 | Erection of 11KV Top cleat with clamp incl supply of Bolts, Nuts & Washers as per Specification and drawing | Each | 180 | 75.2435 | 13543.8336 | 1843.9929 | 15387.8265 | 153.8783 | 2769.8088 | 18311.5136 | Data 24
12 | 1 | Erection of 1.5 Mtrs 11KV Tapping cross Arm made up of 100X50 mm MS Channel and Back Clamp made up of 75X8 mm MS Flat incl supply of Bolts ( 5/8" X 3 "), Nuts & Washers as per Specification and drawing. | Each | 10 | 171.4546 | 1714.5458 | 233.4354 | 1947.9812 | 19.4798 | 350.6366 | 2318.0976 | Data 25
13 | 127 | Erection of all types of fabricated cross arms in complete shape with M.S Channel including M.S Angle struts, M.S Flat Clamps & Fish plates other than V Cross arm and Horizontal cross arm as per the drawing and specification provided by the Engineer In charge as per the field condition after completion of field survey ( Ex: VF, Cut Point , Rising Cross arm , Side arm ..etc) which includes the cost of fabrication charges , paint and other consumables, MS Bolts & Nuts and washers which also includes the cost of labour , transport and stacking charges to the site but excludes the cost of M.S Materials ( M.S Channel , M.S Angle , M.S Flat as required ) | Kgs | 1270 | 278.1956 | 353308.4079 | 48102.9397 | 401411.3477 | 4014.1135 | 72254.0426 | 477679.5037 | Data 21
14 |  | Erection of Line DP Structure/SP structure with 11 KV 400 A AB switch : Fixing of Base channels, Angle struts, Clamps for AB switch structure and operating pipe and earthing as per the drawing which includes the cost of MS Bolts, Nuts & Washers , bentonite powder , Earth Pit Collar (2 ft x 2 ft) , fabrication charges,consumables and labour & transport charges excluding the cost of AB switch and MS Channels, Angles, Flat and GI Pipe & GI Wire No.8 |  |  | 1600.984 | 0 | 0 | 0 | 0 | 0 | 0 | Data 29
14.1 | 0.2 | Line DP structure with AB switch | Each | 2
14.2 | 0.2 | Line SP structure with AB switch ( Whereever erection of DP structure is not feasible) | Each | 2
15 | 3 | Paving out and stringing the 100 Sqmm AAAC over existing supports / newly erected supports and transport to the location and handling charges including pin binding with re-inforcement pieces, jointing, clamping, jumpering an strain insulator binding etc duly maintaining standerd ground clearances and providing sutable size alluminium T clamps wherever jumpering is required and providing sutable alluminium double ferrule wherever mid span jointing is required duly following the technical specification (wherever alluminium T clamps are used , alluminiam tape of 1mm thick is to be wound in 3 layers over the conductor to have better grip and contact). | Conductor KM | 30 | 8655.5458 | 259666.374 | 35353.5768 | 295019.9508 | 2950.1995 | 53103.5911 | 351073.7415 | Data-30
16 | 57 | Fixing of 11 KV Polymer Insulators with pins | Each | 570 | 55.476 | 31621.32 | 4305.2427 | 35926.5627 | 359.2656 | 6466.7813 | 42752.6096 | Data-32
17 | 12 | Fixing of 11 KV Polymer Disc Insulators with metal parts | Each | 120 | 98.5153 | 11821.8408 | 1609.5436 | 13431.3844 | 134.3138 | 2417.6492 | 15983.3475 | Data-33
18 | 21 | Fixing of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp, incl supply of Bolts, Nuts & Washers | Each | 210
19 | 1 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 10 | 68 | 680 | 92.582 | 772.582 | 7.7258 | 139.0648 | 919.3726 | SSR 47.94 Pg No 45
20 | 21 | Numbering of poles with AC Black paint back ground and numbering with white paint including cost of all materials . | Each | 210
21 | 1 | Fixing of LT 5 wire cross arm with back clamps suitable for PSCC poles as per specification incl supply of Bolts, Nuts & Washers | Each | 10
22 | 4 | Fixing of LT Pin insulators with GI Pins as per specification | Each | 40
23 | 5 | Erecton of Guarding with suitable GI wire, along with necessary supporting channels as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules incl supply of Bolts, Nuts & Washers | RMT | 50
|  | Total Ex-works |  |  |  | 3029502.8443 | 412466.8122 | 3441969.6565 | 34419.6966 | 619554.5382 | 4095943.8913
Note : 1. If specifications & drawings are not provided in the Bid document for any BoQ items,, relavant REC specifications & Drawings shall be followed.

## 11KV-11M Spun-supply
BOQ- Supply of Materials for 11 KV Line on 11 mtrs SPUN Poles with 100Sq.mm AAA conductor -For 10 Km
|  |  | Total CKM |  | 10
Line Item No. | 11 mtrs SPUN Poles with 100 Sq.mm per KM Qty | Cost Data Qty | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Quantity for 10 KM | Unit Ex-works price | Total Ex-works Amount | Contractor Profit (Amount) @ 13.615% | Total Amount incl. Contractor Profit | Workers Welfare Cess payable (Amount) @ 1% | GST payable on the price quoted if Contract is awarded (Amount) @18% | Total Amount per line item | SSR Reference
1 |  |  | 2 | 3 | 4 | 5 | 6 = 4x5
1 | 21 | 22 | Supply of 11 M long SPUN pole as per Specification and drawing | Each | 210 | 15754.2373 | 3308389.8305 | 450437.2754 | 3758827.1059 | 37588.2711 | 676588.8791 | 4473004.2561 | Cost Data 2022-23, Sl.No.2 of Section 1(b)-Poles, Pg 4
2 | 4 | 4 | Supply of 9.1M 280Kg WL PSCC Poles as per Specification and drawing | Each | 40 | 4577.1186 | 183084.7458 | 24926.9881 | 208011.7339 | 2080.1173 | 37442.1121 | 247533.9633 | Cost Data 2022-23, Sl.No.5 of Section 1(b)-Poles, Pg 4
3 | 18 | 20 | Supply of 1.07 Mtrs. V 'X' arms for spun poles with curved clamp welding to be done for more grip to the 75x40 MS Channel and Back Clamp with 50X6 mm MS Flat for 11 Mts SPUN Poles as per specification and drawing | Set | 180 | 1274.5961 | 229427.2983 | 31236.5267 | 260663.825 | 2606.6382 | 46919.4885 | 310189.9517 | Data 2A
4 | 18 | 20 | Supply of 11 KV Top Cleat without Clamp as per specification and drawing | Each | 180 | 496.9576 | 89452.3729 | 12178.9406 | 101631.3134 | 1016.3131 | 18293.6364 | 120941.263 | Data 12
5 | 1 | 3 | Supply of 1.5 Mtrs 11KV Tapping cross Arm made up of 100X50 mm MS Channel with curved clamp welding to be done for more grip and Back Clamp made up of 75X8 mm MS Flat for 11 Mts SPUN Poles as per specification and drawing | Each | 10 | 1172.0537 | 11720.5373 | 1595.7512 | 13316.2884 | 133.1629 | 2396.9319 | 15846.3832 | Data 2
6 | 65 | - | Supply of M.S. Channel 75X40 mm as per Technical Specification | Kgs | 650 | 2115.5424 | 1375102.5424 | 187220.2111 | 1562322.7535 | 15623.2275 | 281218.0956 | 1859164.0767 | Data 13
7 | 36.0414 | - | Supply of M.S. Angle 50X50X6 mm as per Technical Specification | Kgs | 360.414 | 4124.8136 | 1486640.5542 | 202406.1115 | 1689046.6656 | 16890.4667 | 304028.3998 | 2009965.5321 | Data 14*2
8 | 30 | - | Supply of M.S. Flat 50X6 mm as per Technical Specification | Kgs | 300 | 2062.4068 | 618722.0339 | 84239.0049 | 702961.0388 | 7029.6104 | 126532.987 | 836523.6362 | Data 14
9 | 2 | 4 | Supply of Stay set with Clamps complete including bow,binding of eye bolts, anchor rods, guy insulators and GI Stay wire 7/3.15 mm (with base plate) as per specification | Each | 20 | 1564.1441 | 31282.8814 | 4259.1643 | 35542.0457 | 355.4205 | 6397.5682 | 42295.0343 | Data -4
10 | 4 |  | Supply of Stay Clamps for 11.0 Mts SPUN pole with 75X8mm MS Flat Including Bolts & Nuts for strut poles | Set | 40
11 | 4 |  | Supply of Stay Clamps for 9.1Mts PSCC Pole with 75X8mm MS Flat Including Bolts & Nuts for Strut poles | Set | 40
12 | 57 | 60 | Supply of 11KV Polymer insulators with pins as per specification. | Each | 570 | 354.2373 | 201915.2542 | 27490.7619 | 229406.0161 | 2294.0602 | 41293.0829 | 272993.1592 | Cost data 2022-23, Sl No 3 of Section 2(b)-11KV Insulators, Pg 6
13 | 12 | 12 | Supply of 11KV Polymer Disc Insulators (B&S) with metal parts (B&S) suitable for 100 Sqmm AAAC as per specification. | Each | 120 | 361.1915 | 43342.9831 | 5901.1471 | 49244.1302 | 492.4413 | 8863.9434 | 58600.5149 | Cost Data 2022-23, Sl.No 7 & 8 of Section 2(b)-11KV Insulators, Pg 6
14 | 21 |  | Supply of Spiral earth coil as per Specification | Each | 210 | 254.4915 | 53443.2203 | 7276.2944 | 60719.5148 | 607.1951 | 10929.5127 | 72256.2226 | Data 29
15 | 3.06 |  | Supply of 100Sq.mm AAA Conductor | KM | 30.6 | 95315.9322 | 2916667.5254 | 397104.2836 | 3313771.809 | 33137.7181 | 596478.9256 | 3943388.4527 | Cost Data 2022-23, Sl.No 5 of Section 4, Pg 9
16 | 8.4 |  | Supply of Aluminium T Clamps for 100sq.mm AAA conductor (6 Nos T Clamps shall be used for each cutpoint, for double jumpering work for cutpoints) | Each | 84
17 | 4.8 |  | Supply Pad Clamps suitable for AB Switch (12 Nos Pad Clamps shall be provided at each AB Switch for double jumpering) | Each | 48
18 | 0.4 |  | Supply of 11 KV Isolators (400 A) double break with Post type Insulator as per specifications and drawing. | Each | 4
19 | 0.4 |  | Supply of 40 mm, 1.8Mts GI Earth Pipe as per Specification and drawing. | Each | 4
20 | 4 |  | Supply of GI wire No.8 as per Specification | Kgs | 40
21 | 21 |  | Supply of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp | Each | 210
22 | 1 | - | Supply of Danger Board 250x200mm for high voltage system, the plate shall be made from mild steel sheet of at least 1.6mm thick and vitreous enameled white, with letters, figures and the conventional skull and cross-bones in signal red colour (refer IS:5-1978) on the front side. The rear side of the plate shall also be enamelled and also the corners of the plate shall be rounded off as per the specification IS:2551-1982 | Each | 10 | 121 | 1210 | 164.7415 | 1374.7415 | 13.7474 | 247.4535 | 1635.9424 | As per Cost Data 2022-23 Item Sub Head 11 Item 20
23 | 1 | - | Supply of LT 3-ph 5 W Cross arm with 50x6 mm MS Back clamps suitable for SPUN Poles as per drawing and specification | Each | 10
24 | 4 | - | Supply of LT Pin Insulators with GI Pins as per specification | Each | 40
25 | 5 | - | Supply of Guarding with suitable GI wire, along with necessary supporting channels as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules . | RMT | 50
|  |  | Total Supply |  |  |  | 10550401.7796 | 1436437.2023 | 11986838.9819 | 119868.3898 | 2157631.0167 | 14264338.3884
Note : 1. If specifications & drawings are not provided in the Bid document for any BoQ items, relavant REC specifications & Drawings shall be followed.
2. For Iron materials only Net weight of the finished products will be considered billing purpose. Bidders are requested to quote the prices of raw materials accordingly.

## 11KV-11M Spun-erection
BOQ- ERECTION of 11 KV Line on 11 mtrs SPUN Poles with 100Sq.mm AAA conductor -For 10 Km
|  | Total CKM |  | 10
Line Item No. | Per kM Qty | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Quantity | Unit price | Total Amount (Excluding Taxes) | Contractor Profit (Amount) @ 13.615% | Total Amount incl. Contractor Profit | Workers Welfare Cess payable (Amount) @ 1% | GST payable on the price quoted if Contract is awarded (Amount) @ 18% | Total Amount per line item | Reference
1 |  | 2 | 3 | 4 | 5 | 6 = 4x5
1 | 1 | Detailed GIS Survey, pit marking and way leaves Clearence including Clearing of heavy jungle, Cutting and removing other kind of trees | KM | 10 | 3883 | 38830 | 5286.7045 | 44116.7045 | 441.167 | 7941.0068 | 52498.8784 | Data-1
2 | 0 | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
2.1 | 4 | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 40 | 426.8 | 17072 | 2324.3528 | 19396.3528 | 193.9635 | 3491.3435 | 23081.6598 | Data-2
2.2 | 20 | 11m Spun Poles (2'6"x2'6"x6' or 0.75mx0.75mx1.8m) | Pit | 200 | 530.2 | 106040 | 14437.346 | 120477.346 | 1204.7735 | 21685.9223 | 143368.0417 | Data-3
3 | 0 | Excavation of pole pit in hard rock by drilling where blasting is not possible
3.1 | 1 | 11m Spun Poles (2'6"x2'6"x6' or 0.75mx0.75mx1.8m) | Pit | 10
4 | 2 | Excavation of Stay pit size 0.45 x 0.45 x 1.34 Mts in all soils except hard murrum and disintegrated rock which requires blasting | Pit | 20 | 194.7 | 3894 | 530.1681 | 4424.1681 | 44.2417 | 796.3503 | 5264.76 | Data-9
5 | 0 | Erection of PSCC/Spun Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
5.1 | 4 | 9.1m/280 KG PSCC Pole | Each | 40 | 4396.997 | 175879.88 | 23946.0457 | 199825.9257 | 1998.2593 | 35968.6666 | 237792.8515 | Data-12
5.2 | 21 | 11m/350KG Spun pole | Each | 210 | 7685.425 | 1613939.25 | 219737.8289 | 1833677.0789 | 18336.7708 | 330061.8742 | 2182075.7239 | Data-15
6 | 2 | Erection of MS Stay Set with HT Guy Insulator and 7/3.15mm GI stay wire Complete as per Drawing where ever necessary including Erection of anchor rod and anchor plate in the pit, and connecting the stay to the pole as per departmental standards but excluding excavation of Stay pit of size 0.45x0.45x1.34Mts incl supply of Bolts, Nuts & Washers. | Each | 20 | 363.6362 | 7272.7248 | 990.1815 | 8262.9063 | 82.6291 | 1487.3231 | 9832.8585 | Data-16
7 | 21 | Concreting of the pole locations of pit size 0.75x0.75x1.8Mts. up to 0.1Mts. as base concrete before erecting the pole and 1.7Mts. upto ground level after erecting the pole as pole cocrete with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary | Each | 210 | 6946.0417 | 1458668.75 | 198597.7503 | 1657266.5003 | 16572.665 | 298307.9701 | 1972147.1354 | Data-17
8 | 2 | Concreting of 33KV/11KV/LT Stay locations wherever necessary for anchor rod of the stay set up to ground level of size 0.45x0.45x1.34Mts. with 1:3:6 cement concreting mix using 20 mm and 12mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring, including seigniorage charges and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. | Each | 20 | 1936 | 38720 | 5271.728 | 43991.728 | 439.9173 | 7918.511 | 52350.1563 | Data-19
9 | 18 | Erection of 1.07 Mtrs. V 'X' arms for spun poles with curved clamp welding to be done for more grip to the 75x40 mm MS Channel and Back Clamp with 50X6 mm MS Flat incl. supply of Bolts ( 5/8" X 3 ") , Nuts & Washers as per Specification and drawing | Each | 180 | 163.3588 | 29404.584 | 4003.4341 | 33408.0181 | 334.0802 | 6013.4433 | 39755.5416 | Data-20
10 | 18 | Erection of 11KV Top cleat incl supply of Bolts, Nuts & Washers as per Specification and drawing | Each | 180 | 75.2435 | 13543.8336 | 1843.9929 | 15387.8265 | 153.8783 | 2769.8088 | 18311.5136 | Data 24
11 | 1 | Erection of 1.5 Mtrs 11KV Tapping cross Arm made up of 100X50 mm MS Channel and Back Clamp made up of 75X8 mm MS Flat incl. supply of Bolts ( 5/8" X 3 ") , Nuts & Washers as per Specification and drawing. | Each | 10 | 171.4546 | 1714.5458 | 233.4354 | 1947.9812 | 19.4798 | 350.6366 | 2318.0976 | Data 25
12 | 131 | Erection of all types of fabricated cross arms in complete shape with M.S Channel including M.S Angle struts, M.S Flat Clamps & Fish plates other than V Cross arm and Horizontal cross arm as per the drawing and specification provided by the Engineer In charge as per the field condition after completion of field survey ( Ex: VF, Cut Point , Rising Cross arm , Side arm ..etc) which includes the cost of fabrication charges , paint and other consumables, MS Bolts & Nuts and washers which also includes the cost of labour , transport and stacking charges to the site but excludes the cost of M.S Materials ( M.S Channel , M.S Angle , M.S Flat as required ) | Kgs | 1310 | 278.1956 | 364436.2318 | 49617.993 | 414054.2248 | 4140.5422 | 74529.7605 | 492724.5275 | Data 21
13 |  | Erection of Line DP Structure/SP structure with 11 KV 400 A AB switch : Fixing of Base channels, Angle struts, Clamps for AB switch structure and operating pipe and earthing as per the drawing which includes the cost of MS Bolts, Nuts & Washers , bentonite powder , Earth Pit collar (2 ft x 2 ft) , fabrication charges,consumables and labour & transport charges excluding the cost of AB switch and MS Channels, Angles, Flat and GI Pipe & GI Wire No.8. |  | 0 | 1600.984 | 0 | 0 | 0 | 0 | 0 | 0 | Data 29
13.1 | 0.2 | Line DP structure with AB switch | Each | 2
13.2 | 0.2 | Line SP structure with AB switch ( Whereever erection of DP structure is not feasible) | Each | 2
14 | 3 | Paving out and stringing the 100 Sqmm AAAC over existing supports / newly erected supports and transport to the location and handling charges including pin binding with re-inforcement pieces, jointing, clamping, jumpering an strain insulator binding etc duly maintaining standerd ground clearances and providing sutable size alluminium T clamps wherever jumpering is required and providing sutable alluminium double ferrule wherever mid span jointing is required duly following the technical specification (wherever alluminium T clamps are used , alluminiam tape of 1mm thick is to be wound in 3 layers over the conductor to have better grip and contact). | Conductor KM | 30 | 8655.5458 | 259666.374 | 35353.5768 | 295019.9508 | 2950.1995 | 53103.5911 | 351073.7415 | Data-30
15 | 57 | Fixing of 11 KV Polymer Insulators with pins | Each | 570 | 55.476 | 31621.32 | 4305.2427 | 35926.5627 | 359.2656 | 6466.7813 | 42752.6096 | Data-32
16 | 12 | Fixing of 11 KV Polymer Disc Insulators with metal parts | Each | 120 | 98.5153 | 11821.8408 | 1609.5436 | 13431.3844 | 134.3138 | 2417.6492 | 15983.3475 | Data-33
17 | 21 | Fixing of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp, incl supply of Bolts , Nuts & Washers for all the poles | Each | 210
18 | 1 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 10 | 68 | 680 | 92.582 | 772.582 | 7.7258 | 139.0648 | 919.3726 | SSR 47.94 Pg No 45
19 | 21 | Numbering of poles with AC Black paint back ground and numbering with white paint including cost of all materials . | Each | 210
20 | 1 | Fixing of LT 5 wire cross arm with back clamps suitable for SPUN poles as per specification incl supply of Bolts , Nuts & Washers | Each | 10
21 | 4 | Fixing of LT Pin insulators with GI Pins as per specification | Each | 40
22 | 5 | Erecton of Guarding with suitable GI wire, along with necessary supporting channels as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules incl supply of Bolts , Nuts & Washers . | RMT | 50
|  | Total Ex-works |  |  |  | 4173205.3348 | 568181.9063 | 4741387.2411 | 47413.8724 | 853449.7034 | 5642250.817
Note : 1.If specifications & drawings are not provided in the Bid document for any BoQ items,, relavant REC specifications & Drawings shall be followed.

## 33 KV-12.5M Spun-Supply
BoQ - Supply of material for 33KV Overhead Lines with 100sq.mm. AAA Conductor over 12.5Mtrs SPUN Poles
[5 empty] | KM | 10
Sl. No | Description as per Previous Agreement | Qty per KM | Cost Data Qty | Description of Goods (including inland transportation, Loading & unloading and other services required in India to convey the goods to their final destination) | Unit | Qty per 10 KM
1 | 12.5 Mts./350 Kgs Spun Poles | 18 | 18 | Supply of 12.5 Mts./350 Kgs Spun Poles as per specification and drawing. | Each | 180
2 | 9.1 Mts/280 Kgs. PSCC Poles | 6 | 4 | Supply of 9.1 Mts./280 Kgs PSCC Poles as per specification and drawing. | Each | 60
3 | 33 KV 1.53 M 'V' Cross Arm ( GI Channel ) without clamp | 16 | 16 | Supply of 33KV V cross arm with 100x50mm MS channel with curved clamp welding to be done for more grip and Back Clamp with 75x8mm MS flat for 12.5/11mts spun poles as per Specification and drawing. | Each | 160
4 | 33 KV GI Top cleat without clamp | 16 | 16 | Supply of 33KV top cleat (65x65x6mm MS angle) without Backclamp for 12.5/11 Mts Spun poles as per specification and drawing. | Each | 160
5 |  | 1 | 3 | Supply of Horizontal Cross arm with 100x50mm MS channel with curved clamp welding to be done for more grip and Back clamp with 75X8mm MS Flat as per specification and drawing |  | 10
6 |  | 122 |  | Supply of M.S. Channel 100X50 mm as per Technical Specification | Kgs | 1220
7 |  | 44 |  | Supply of M.S. Angle 65X65X6 mm as per Technical Specification | Kgs | 440
8 |  | 58 |  | Supply of M.S. Flat 75X8 mm as per Technical Specification | Kgs | 580
9 |  | 6 |  | Supply of Stay Clamps with 75X8mm MS Flat Including Bolts & Nuts for 12.5 Mts SPUN pole for strut poles | Set | 60
10 |  | 6 |  | Supply of Stay Clamps with 75X8mm MS Flat Including Bolts & Nuts for 9.1Mts PSCC Pole for strut poles | Set | 60
11 | 33 KV Polymer Insulator with Pins | 51 | 48 | Supply of 33 KV Polymer Pin Insulator with GI Pins as per Specification and drawing. | Each | 510
12 | 33 KV Polymer Disc Insulators | 15 | 12 | Supply of 33 KV Polymer Disc Insulators with metal parts ( B&S Type) as per Specification and drawing.. | Each | 150
13 | 100 Sq.mm AAA Conductor | 3.06 | 3.06 | Supply of 100 Sqmm AAAConductor as per Specification and drawing. | Km | 30.6
14 |  | 12 |  | Supply of Aluminium T Clamps for 100sq.mm AAA conductor as per Specification and drawing. (6 Nos T Clamps shall be used for each cutpoint , for double jumpering work for cutpoints) | Each | 120
15 |  | 4.8 |  | Supply Pad Clamps suitable for AB Switch (12 Nos Pad Clamps shall be provided at each AB Switch for double jumpering) | Each | 48
16 | 33 KV 800 A AB Switches | 0.4 |  | Supply of 33 KV 800 A double break pipe type AB Switch as per Specification and drawing. | Nos | 4
17 | 40 mm, 1.8Mts GI Earth Pipe | 0.4 |  | Supply of 40 mm, 1.8Mts GI Earth Pipe as per Specification and drawing. | Nos | 4
18 | GI Wire No:8 | 4 |  | Supply of GI wire No.8 as per Specification | Kgs | 40
19 |  | 18 |  | Supply of Spiral earth coil as per Specification and drawing. | Nos | 180
20 | Danger Boards fabricated with MS Sheet of size minimum 250x200mm and thickness minimum 1.6 mm with conventional skull and cross-bones in accordance with IS:2551-1982 or the latest version | 1 |  | Supply of Danger Boards fabricated with MS Sheet of size minimum 250x200mm and thickness minimum 1.6 mm with conventional skull and cross-bones in accordance with IS:2551-1982 or the latest version | Each | 10
21 |  | 1 | - | 11 KV Horizontal Cross Arm with 75 X 40 mm MS Channel with curved clamp welding to be done for more grip with 50x6 mm MS Back Clamp and MS Back clamp with 50 x6 mm MS Flat | Each | 10
22 |  | 3 | - | Supply of 11 KV Polymer Pin Insulators with GI Pins as per specification | Each | 30
23 |  | 1 | - | Supply of LT 3-ph 5 W Cross arm with 50x6 mm MS Back clamps suitable for SPUN Poles as per drawing and specification | Each | 10
24 |  | 4 | - | Supply of LT Pin Insulators with GI Pins as per specification | Each | 40
25 |  | 18 |  | Supply of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp suitable for 12.5 Mts SPUN Pole |  | 180
26 |  | 5 |  | Supply of Guarding with suitable GI wire, along with necessary supporting channels as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules . | RMT | 50
Note : 1. If specifications & drawings are not provided in the Bid document for any BoQ items, relavant REC specifications & Drawings shall be followed.
2. For Iron materials only Net weight of the finished products will be considered billing purpose. Bidders are requested to quote the prices of raw materials accordingly.

## 33 KV-12.5M Spun-erection
BOQ- ERECTION of 33 KV Line on 12.5 mtrs SPUN Poles with 100Sq.mm AAA conductor -For 10 Km
|  |  |  | KM | 10
Sl. No | Qty per KM | Description as per Previous Agreement | Description of Related Services (excludes inland transportation and other services required in India to convey the goods to their final destination) | Unit | Qty per 10 KM
1 | 1 | Detailed Survey, pit marking and way leaves Clearence including Clearing of heavy jungle. | Detailed GIS Survey, pit marking and way leaves Clearence including Clearing of heavy jungle, Cutting and removing other kind of trees | Km | 10
2 |  |  | Excavation of pits in all soils, i.e, mixture of gravel and soft disintegrated rock like shales ordinary gravel, stony earth and earth mixed with fair sized boulders except hard rock which requires blasting and drilling.
2.1 | 6 |  | For 9.1m PSCC Poles ( Size of pit is 2'x2'x5' or 0.6mx0.6mx1.5m) | Pit | 60
2.2 | 17 |  | 12.5m Spun Poles (2'6"x2'6"x7' or 0.75mx0.75mx2.1m) | Pit | 170
3 |  |  | Excavation of pole pit in hard rock by drilling where blasting is not possible
3.1 | 1 |  | 12.5m Spun Poles (2'6"x2'6"x7' or 0.75mx0.75mx2.1m) | Pit | 10
4 |  |  | Erection of PSCC/Spun Poles in position, aligning and setting to work as per specification including supply of labour, T&P, back filling the earth, ramming for consolidation,Cost of transportation of Pole of up to pit location fixing earth coils wherever necessary and Geotagging of all all poles -Locating Co-ordinates(Lattitude & Longitude) using GPS as per Technical specification but excluding the cost of pit excavation.
4.1 | 6 | Erection of 12.5Mtrs.Spun poles including earth coils complete without hardware wherever necessary (but excluding the cost of pit excavation, concreting and backfilling) | 9.1m/280 KG PSCC Pole | Each | 60
4.2 | 18 | Erection of 11Mtrs.Spun poles including earth coils complete without hardware wherever necessary (but excluding the cost of pit excavation, concreting and backfilling) | 12.5 Mts SPUN Poles | Each | 180
5 | 18 | Concreting of the pole locations of pit size 0.75x0.75x2.1Mts. up to 0.1Mts. as base concrete before erecting the pole and 2Mts. upto ground level after erecting the pole as pole concrete for 12.5 Mtr Spun pole with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary (new or existing) | Concreting of the pole locations of pit size 0.75x0.75x2.1Mts. up to 0.1Mts. as base concrete before erecting the pole and 2Mts. upto ground level after erecting the pole as pole concrete for 12.5 Mtr Spun pole with 1:3:6 cement concreting mix using 20mm HBG metal including cost of all the materials i.e. cement, sand, HBG metal etc. including dewatering, shoring & shuttiring and curing after concreting as per technical specification including DPs & Single Pole Structures and other location wherever necessary. | Each | 180
6 | 16 | Fixing of 33KV GI V cross arm/GI Channel Crossarm and GI Back Clamps including of fabrication charges with 2 Nos 33KV Polymer Type Pin Insulators with Pin,Pin binding as per Specification | Erection of 33KV V cross arm with 100x50mm MS channel and Back Clamp with 75x8mm MS flat incl. Cost of Bolts , Nuts and washers as per Specification and drawing. | Each | 160
7 | 16 | Fixing of 33KV GI top cleat with GI clamp including of fabrication charges along with 1No 33KV Polymer type Pin Insulator with Pin ,Pin binding as per specification | Erection of 33KV top cleat (65x65x6mm MS angle) with clamp incl. Cost of Bolts , Nuts and washers as per specification and drawing | Each | 160
8 | 1 | Providing of Horizontal Cross arm with A type pedastal including of fabrication charges, pin insulators complete with hardware wherever necessary on existing/erected poles | Erection of Horizontal Cross arm with 100x50mm MS channel and Back clamp with 75X8mm MS Flat incl. supply of Bolts , Nuts & washers as per specification and drawing | Each | 10
9 | 224 | Providing of 33KV T Raiser with 100X50mm GI channel of 1.51Mts. vertical and 2.15Mts. horizontal with A type Pedastals with 75X8mm GI Flat and Back Clamps including of fabrication charges with 3Nos 33KV polymer Pin Insulators with pin incl Pin binding with re-inforcement pieces and coil earthing as per Specification where ever necessary as per directions of the Engineer In charge | Erection of all types of fabricated cross arms in complete shape with M.S Channel including M.S Angle struts, M.S Flat Clamps & Fish plates other than V Cross arm and Horizontal cross arm as per the drawing and specification provided by the Engineer In charge as per the field condition after completion of field survey ( Ex: VF, Cut Point , Rising Cross arm , Side arm ..etc) which includes the cost of fabrication charges , paint and other consumables, MS Bolts & Nuts and washers which also includes the cost of labour , transport and stacking charges to the site but excludes the cost of M.S Materials ( M.S Channel , M.S Angle , M.S Flat as required) | Kgs | 2240
10 | 51 | Erection of 3 sets of 33KV Polymer Discs with Metal Parts to the existing Supports as per Specification | Fixing of 33 KV Polymer Disc Insulators with metal parts | Each | 510
11 | 15 | Erection of 3 sets of 33KV Polymer insulators with G I pin to the existing Supports as per Specification | Fixing of 33 KV Polymer Insulators with pin | Each | 150
12 | 3 | Paving out and stringing the 100 Sqmm AAAC (1 Wire) over existing supports / newly erected supports and transport to the location and handling charges including pin binding, jointing, clamping, jumpering an strain insulator binding etc duly maintaining standerd ground clearances and providing sutable size aluminium T clamps wherever jumpering is required and providing sutable aluminium double ferrule wherever mid span jointing is required duly following the technical specification (wherever aluminium T clamps are used , aluminium tape of 1mm thick is to be wound in 3 layers over the conductor to have better grip and contact) | Paving out and stringing the 100 Sqmm AAAC (1 Wire) over existing supports / newly erected supports and transport to the location and handling charges including pin binding with re-inforcement pieces , jointing, clamping, double jumpering and strain insulator binding etc duly maintaining ground clearances as per IE rule and providing sutable size aluminium T clamps wherever jumpering is required and providing sutable aluminium double ferrule wherever mid span jointing is required duly following the technical specification (wherever aluminium T clamps are used , aluminium tape of 1mm thick is to be wound in 3 layers over the conductor to have better grip and contact) | km | 30
13 |  |  | Erection of 33 KV Line DP Structure : Fixing of Base channels, Angle struts, Clamps for AB switch structure and operating pipe and earthing as per the drawing which includes the cost of MS Bolts, Nuts & Washers , bentonite powder , Earth pit collar (2 ft x 2 ft ), fabrication charges,consumables and labour & transport charges excluding the cost of AB switch and MS Channels, Angles, Flat and GI Pipe & GI Wire No.8.
13.1 | 0.2 |  | Line D.P. with A.B.Switch over 12.5 Mts Spun poles with AB switch . | Each | 2
13.2 | 0.2 |  | Line D.P. without A.B.Switch over 12.5 Mts Spun poles with 3 Nos. 33KV Polymer Pin Insulator with GI Pins | Each | 2
14 | 18 | Numbering of poles with white paint and AC black paint as back ground including supply of materials | Numbering of poles with white paint and AC black paint as back ground including supply of materials | Each | 180
15 | 1 |  | Erection of 11 KV Horizontal Cross Arm with 75 X 40 mm MS Channel with curved clamp welding to be done for more grip with 50x6 mm MS Back Clamp and MS Back clamp with 50 x6 mm MS Flat incl. supply of Bolts ( 5/8" X 3 ") , Nuts & Washers | Each | 10
16 | 3 |  | Fixing of 11 KV Polymer Insulators with pin binding with re-inforcement pieces | Each | 30
17 | 1 |  | Fixing of LT 3-Ph 5 wire cross arm with back clamps suitable for SPUN poles as per specification incl supply of Bolts , Nuts & Washers | Each | 10
18 | 4 |  | Fixing of LT Pin insulators with GI Pins as per specification | Each | 40
19 | 18 | Fixing of Foot Cross arm with 50X50X6 mm GI angle of 0.79Mts.(2feet 6 inches) Long with Back Clamp including of fabrication charges | Fixing of Foot Cross arm with 50X50X6 mm MS Angle of 0.61Mts.(2feet) Long with Back Clamp, incl supply of Bolts , Nuts & Washers for all the poles | Each | 180
20 | 1 | Supply and Fixing of Danger Notice Board of size 250x200mm for high voltage system, the plate shall be made from mild steel sheet of at least 1.6mm thick and vitreous enameled white, with letters, figures and the conventional skull and cross-bones in signal red colour (refer IS:5-1978) on the front side. The rear side of the plate shall also be enamelled and also the corners of the plate shall be rounded off as per the specification IS:2551-1982 | Fixing of Danger Notice Board of size 250x200mm for high voltage system incl supply of Bolts , Nuts & Washers | Each | 10
21 | 5 |  | Erecton of Guarding with suitable GI wire, along with necessary supporting channels as per specifications at all the crossings of over-head power lines with roads and telecommunication lines whereever mandatatory as per safety rules incl supply of Bolts , Nuts & Washers . | RMT | 50
Note : 1.If specifications & drawings are not provided in the Bid document for any BoQ items,, relavant REC specifications & Drawings shall be followed.